## Results over 10 ugl lead
Details of Operational Action AW caried out.
Date/time | Area | Post code | Sample point name | Lead - NFVS (ug/l) | Lead - flushed (ug/l) | Communication Pipe | Supply Pipe
2024-01-23 12:34 | Norwich | NR3 1 | Heigham PWSZ Customer Tap | 19.694 | 6.305 | Replaced | N/A
2024-01-24 08:45 | Norwich | NR1 1 | Heigham PWSZ Customer Tap | 87.858* | 0.951 | Replaced | N/A
2024-01-30 14:33 | Norwich | NR3 1 | Heigham PWSZ Customer Tap | 27.394 | 5.586 | Replaced | N/A
2024-06-18 12:36 | Norwich | NR2 3 | Heigham PWSZ Customer Tap | 25.864 | 5.593 | Scheduled for replacement | N/A
2024-08-22 12:27 | Norwich | NR1 4 | Heigham PWSZ Customer Tap | 310.691 | 1.995 | Replaced | N/A
2024-03-06 09:47 | Kings Lynn | PE30 5 | Kings Lynn PWSZ customer tap | 13.41 | 2.206 | Not lead | N/A
2024-03-11 09:55 | Kings Lynn | PE30 5 | Kings Lynn PWSZ customer tap | 14.417 | 1.759 |  | N/A
2024-09-04 11:20 | Kings Lynn | PE30 1 | Kings Lynn PWSZ customer tap | 12.854 | 5.029 | Replaced | N/A
2024-01-11 14:10 | Norwich | NR4 7 | Lakenham PWSZ Customer Tap | 28.826 | 16.093 |  | N/A
2024-02-06 09:17 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 21.804 | 3.126 | Replaced | Replaced to POE
2024-04-03 09:21 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 25.165 | 1.516 | Replaced | Replaced to POE
2024-04-03 11:30 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 13.308 | 2.499 | Not lead | Replaced to POE
2024-04-08 09:15 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 12.042 | 2.449 | Replaced | Supply pipe not changed as part of planned work trial
2024-04-10 14:15 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 14.008 | 2.281 | Replaced | Customer did not take us up on the offer of a free supply pipe replacement
2024-04-18 08:35 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 11.031 | 1.845 | Not lead | Replaced to POE
2024-04-22 13:25 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 622.952* | 3.258 | Replaced | Replaced to POE
2024-05-13 13:42 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 15.362 | 1.709 | Replaced | Customer did not take us up on the offer of a free supply pipe replacement
2024-05-17 09:15 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 10.98 | 3.64 | Replaced | Customer did not take us up on the offer of a free supply pipe replacement
2024-06-17 09:10 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 13.163 | 11.203 | Replaced | N/A
2024-06-26 10:11 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 14.623 | 4.187 | Replaced | Replaced to POE
2024-07-03 12:53 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 13.915 | 6.627 | Replaced | N/A
2024-08-21 07:10 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 15.85 | 2.974 | Replaced | Replaced to POE
2024-10-22 13:25 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 10.065 | 2.505 | Scheduled for replacement | N/A
2024-10-28 10:56 | Norwich | NR4 7 | Lakenham PWSZ Customer Tap | 11.478 | 0.16 | Not lead | N/A
2024-11-13 10:19 | Norwich | NR2 3 | Lakenham PWSZ Customer Tap | 12.604 | 2.725 | Replaced | Replaced to POE
2024-11-18 11:41 | Norwich | NR2 3 | Lakenham PWSZ Customer Tap | 14.124 | 2.832 | Replaced | Replaced to POE
2024-11-19 13:25 | Norwich | NR2 3 | Lakenham PWSZ Customer Tap | 17.243 | 2.708 | Replaced | N/A
2024-11-25 11:39 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 14.456 | 2.294 | Replaced | Replaced to POE
2024-11-26 10:30 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 11.377 | 2.998 | Scheduled for replacement | N/A
2024-11-26 13:38 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 13.254* | 1.575 | Replaced | Replaced to POE
2024-11-26 14:48 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 11.96 | 1.549 | Replaced | Customer did not take us up on the offer of a free supply pipe replacement
2024-12-12 10:11 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 10.756* | 4.766 | Scheduled for replacement | Replaced to POE
2024-12-13 11:45 | Norwich | NR2 2 | Lakenham PWSZ Customer Tap | 20.037 | 2.213 | Replaced | Supply pipe not changed as part of planned work trial
2024-01-30 14:14 | Norwich | NR6 6 | Mancroft PWSZ Customer Tap | 20.036 | 2.818 | Replaced | N/A
2024-02-05 12:48 | Norwich | NR6 5 | Mancroft PWSZ Customer Tap | 10.526 | 1.557 | Scheduled for replacement | N/A
2024-02-29 09:00 | Norwich | NR6 6 | Mancroft PWSZ Customer Tap | 10.072 | 2.019 | Replaced | N/A
2024-08-16 13:19 | Norwich | NR6 6 | Mancroft PWSZ Customer Tap | 15.391 | 7.481 | Scheduled for replacement | N/A
2024-08-23 13:51 | Norwich | NR6 5 | Mancroft PWSZ Customer Tap | 10.206 | 3.428 | Scheduled for replacement | N/A
2024-11-14 11:30 | Norwich | NR6 7 | Mancroft PWSZ Customer Tap | 10.501* | 0.202 | Scheduled for replacement | N/A
2024-12-03 08:11 | Norwich | NR3 3 | Mancroft PWSZ Customer Tap | 14.649 | 1.393 | Not lead | N/A
2024-03-21 12:30 | Norwich | NR1 4 | Plumstead PWSZ Customer Tap | 14.104 | 6.581 | Replaced | N/A
2024-04-08 14:28 | Norwich | NR1 4 | Plumstead PWSZ Customer Tap | 14.163 | 9.424 | Replaced | N/A
2024-06-11 13:45 | Norwich | NR7 8 | Plumstead PWSZ Customer Tap | 14.933 | 3.38 | Replaced | N/A
2024-08-15 14:36 | Norwich | NR7 0 | Plumstead PWSZ Customer Tap | 10.929 | 3.666 | Scheduled for replacement | N/A
2024-08-19 17:26 | Norwich | NR7 0 | Plumstead PWSZ Customer Tap | 23.383 | 6.019 |  | N/A
2024-10-28 10:05 | Norwich | NR1 4 | Plumstead PWSZ Customer Tap | 11.463 | 2.23 | Scheduled for replacement | N/A
2024-06-14 09:55 | Norwich | NR7 8 | Postwick PWSZ customer tap | 15.444 | 3.048 | Replaced | N/A
2024-07-29 12:05 | Norwich | NR1 4 | Postwick PWSZ customer tap | 10.972 | 6.618 | Replaced | N/A
2024-10-10 09:50 | Norwich | NR7 0 | Postwick PWSZ customer tap | 19.897 | 8.311 | Scheduled for replacement | N/A
2024-10-18 09:00 | Norwich | NR7 8 | Postwick PWSZ customer tap | 21.559 | 2.133 | Scheduled for replacement | N/A
2024-10-24 12:27 | Norwich | NR7 8 | Postwick PWSZ customer tap | 165.034 | 1.509 | Replaced | N/A
2024-11-04 12:27 | Norwich | NR1 4 | Postwick PWSZ customer tap | 11.576 | 1.943 | Scheduled for replacement | N/A
|  |  |  | * Lead solder confirmed |  |  | POE =Point of Entry into customer's property
N/A = Not part of the planned work project so no action taken by AW