## Sheet1
Site | Date | Reason for EDM Activation
Colchester-Royal Ldn Mboro Pumping Station | 2023-11-10 | Power outage, tanker deployed, flows controlled - EDM activated but following investigation no discharge to environment confirmed
Colchester-Royal Ldn Mboro Pumping Station | 2023-12-07 | No discharge, site operating normally but suffered issue with telemetry data. - EDM activated but following investigation no discharge to environment confirmed
Holme - Beech Road Pumping Station | 2023-03-21 09:45 | Planned maintenance bathing water operational check- EDM activated but following investigation no discharge to environment confirmed
Holme - Beech Road Pumping Station | 2023-09-20 23:13 | Spill occurred due to surface water/ storm water inundation into the network causing a spill during heavy rainfall event
Holme - Beech Road Pumping Station | 2023-09-21 02:36
Holme - Beech Road Pumping Station | 2023-10-20 12:40
Holme - Beech Road Pumping Station | 2023-10-21 07:30
Holme - Beech Road Pumping Station | 2023-10-22 05:35
Holme - Beech Road Pumping Station | 2023-12-12 19:57
Holme - Beech Road Pumping Station | 2023-12-13 13:23
Holme - Beech Road Pumping Station | 2023-12-19 08:04
Holme - Beech Road Pumping Station | 2023-12-20 05:16
Peldon Mersea Road Pumping Station | 2023-01-12 | Spill occurred due to surface water/ storm water inundation into the network causing a spill during heavy rainfall event. Scheme due for completion Mar 25 to remove 40 misconnected surface water connections from private property. Equivalent of foul sewage from 4000 homes.
Peldon Mersea Road Pumping Station | 2023-01-16
Peldon Mersea Road Pumping Station | 2023-03-10
Peldon Mersea Road Pumping Station | 2023-03-17
Peldon Mersea Road Pumping Station | 2023-03-26
Peldon Mersea Road Pumping Station | 2023-03-29
Peldon Mersea Road Pumping Station | 2023-03-31
Peldon Mersea Road Pumping Station | 2023-07-04
Peldon Mersea Road Pumping Station | 2023-07-26
Peldon Mersea Road Pumping Station | 2023-07-27
Peldon Mersea Road Pumping Station | 2023-08-02 | Pump fault. Both pumps tripped and reset. Samples taken and no impact to the environment
Peldon Mersea Road Pumping Station | 2023-08-05 | Spill occurred due to surface water/ storm water inundation into the network causing a spill during heavy rainfall event. Scheme due for completion Mar 25 to remove 40 Misconnected surface water connections from private property. Equivalent of foul sewage from 4000 homes.
Peldon Mersea Road Pumping Station | 2023-08-18
Peldon Mersea Road Pumping Station | 2023-08-19
Peldon Mersea Road Pumping Station | 2023-10-03 | Suspect that EDM was activated but following investigation no discharge to environment confirmed as there was a maintenance visit at the same time as the event
Peldon Mersea Road Pumping Station | 2023-10-18 | Spill occurred due to surface water/ storm water inundation into the network causing a spill during heavy rainfall event. Scheme due for completion Mar 25 to remove 40 misconnected surface water connections from private property. Equivalent of foul sewage from 4000 homes.
Peldon Mersea Road Pumping Station | 2023-10-20
Peldon Mersea Road Pumping Station | 2023-10-29
Peldon Mersea Road Pumping Station | 2023-11-02
Peldon Mersea Road Pumping Station | 2023-11-03
Peldon Mersea Road Pumping Station | 2023-11-13
Peldon Mersea Road Pumping Station | 2023-11-14
Peldon Mersea Road Pumping Station | 2023-11-27
Peldon Mersea Road Pumping Station | 2023-12-07 | Both pumps stopped due to mains power fail during storm conditions
Peldon Mersea Road Pumping Station | 2023-12-09 | Spill occurred due to surface water/ storm water inundation into the network causing a spill during heavy rainfall event. Scheme due for completion Mar 25 to remove 40 misconnected surface water connections from private property. Equivalent of foul sewage from 4000 homes.
Peldon Mersea Road Pumping Station | 2023-12-12
Peldon Mersea Road Pumping Station | 2023-12-19
Peldon Mersea Road Pumping Station | 2023-12-31
Rochford Depot Pumping Station | 2023-01-16 | Storm overflow operated during storm conditions
Rochford Depot Pumping Station | 2023-03-09
Rochford Depot Pumping Station | 2023-10-24
Rochford Depot Pumping Station | 2023-11-02
Rochford Depot Pumping Station | 2023-11-13
Rochford Depot Pumping Station | 2023-11-14
Rochford Depot Pumping Station | 2023-12-09
Rochford Depot Pumping Station | 2023-12-12 | Intermittent pump failures during storm event. Pumps reset by operator. No visual impact to environment reported by the operator.
Rochford Depot Pumping Station | 2023-12-13
Rochford Depot Pumping Station | 2023-12-15
Rochford Depot Pumping Station | 2023-12-16
Rochford Depot Pumping Station | 2023-12-19 | Storm overflow operated during storm conditions
Sea Palling Clink Road Pumping Station | 2023-10-11 | Short term power failure, floats fail safe, so show as in alarm - EDM activated but following investigation no discharge to environment confirmed
Sea Palling Waxham Road Pumping Station | 2023-10-13
Southend - Towerfield Pumping Station | 2023-01-25 | Spill occurred due to surface water/ storm water inundation into the network causing a spill during heavy rainfall event.
Southend - Towerfield Pumping Station | 2023-03-02 | EDM activated but following investigation no discharge to environment confirmed
Southend - Towerfield Pumping Station | 2023-03-02
Southend - Towerfield Pumping Station | 2023-03-02
Southend - Towerfield Pumping Station | 2023-04-03 | Pump fault due to an airlock. Samples taken and no impact to the environment
Southend - Towerfield Pumping Station | 2023-04-05
Southend - Towerfield Pumping Station | 2023-04-06
Southend - Towerfield Pumping Station | 2023-11-24 | EDM activated but following investigation no discharge to environment confirmed
Formulas:
Date = '[1]Towerfield -AC'!N2