## Overview
PR24 Enhancement Cost breakdowns We provide the following detailed cost breakdowns to support our Representations relating to the enhancement strategies outlined in column B. Columns C and D outline the document and section where further narrative relating to these cost breakdowns can be found
Enhancement Strategy | Relevant document | Section
Sludge enhancement (Chapter 3) | ANH_DD_020 Carbon neutral PR24 DD Representation enhancement strategy | 3.3
Resilience (water) (Chapter 8) | ANH_DD_018 Resilient to flood PR24 DD Representation enhancement strategy | 8.3.3
Odour and Resilience (water recycling) (Chapter 9) | ANH_DD_018 Resilient to flood PR24 DD Representation enhancement strategy | 9.4.1
Security (water & water recycling) (Chapter 10) | ANH_DD_018 Resilient to flood PR24 DD Representation enhancement strategy | 10.3.3
Addressing raw water deterioration (Chapter 11) | ANH_DD_018 Resilient to flood PR24 DD Representation enhancement strategy | 11.3.2, 11.3.3
Increasing FFTs (Chapter 6) | ANH_DD_018 Resilient to flood PR24 DD Representation enhancement strategy | 6.3
Microbiological treatment (Chapter 6) | ANH_DD_021 Sustainable growth PR24 DD Representation enhancement strategy | 6.3.2
Microbiological treatment (Cost benefit) (Chapter 6) | ANH_DD_021 Sustainable growth PR24 DD Representation enhancement strategy | 6.3.3
Nutrient and sanitary parameters (Chapter 3) | ANH_DD_019 Work with others to achieve significant improvements in ecological quality of catchments | 3.3.3
Nutrient and sanitary parameters (Cost benefit) (Chapter 3) | ANH_DD_019 Work with others to achieve significant improvements in ecological quality of catchments | 3.3.3
Supply side improvements (recirculation and Marham) (Chapter 3) | ANH_DD_018 Resilient to flood PR24 DD Representation enhancement strategy | 3.3.1

## Sludge Enhancement
the cost show are total costs including Labour, Plant, materials and prelims, Location factors and On costs
Investment ID | I033831
Investment Title | Regional sludge treatment capacity
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 204561 | Total Installed Power | 32 | kW
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 55633.156 | Total Installed Power | 32 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E <#2> | 2A - Catchment Pumping | 1 | New | 204561 | Total Installed Power | 32 | kW
Pumping Stations, Interprocess - Civil <#2> | 2A - Catchment Pumping | 1 | New | 55633.156 | Total Installed Power | 32 | kW
Pumping Stations, Interprocess - Civil <#3> | 2A - Catchment Pumping | 1 | New | 39433.7851 | Total Installed Power | 10 | kW
Pumps, Thickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 318789.3572 | Total Installed Power | 54 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E <#3> | 2A - Catchment Pumping | 1 | New | 76532 | Total Installed Power | 10 | kW
Pumps, Thickened Sludge - M&E <#2> | 2A - Catchment Pumping | 1 | New | 286770.7109 | Total Installed Power | 44 | kW
Aeration, Fine Bubble Diffusers | 2D - Primary Treatment | 1 | New | 1155772.4366 | Total Volume | 2000 | m3
Aeration Tanks, Rectangular - Civil | 2D - Primary Treatment | 1 | New | 890750.9586 | Total Volume | 2000 | m3
Aeration Tanks, Rectangular - Civil <#2> | 2D - Primary Treatment | 1 | New | 446671.5932 | Total Volume | 400 | m3
Phosphate Removal | 2D - Primary Treatment | 2 | New | 666937.24 | Flow | 500 | m3/d
Final Tanks Scrapers, Circular - M&E | 2E - Secondary Treatment | 1 | New | 279044.8105 | Total Volume | 380 | m3
Final Tanks, Circular - Civil | 2E - Secondary Treatment | 1 | New | 442683.2752 | Total Volume | 380 | m3
Sludge Mixers - M&E | 2F - Sludge Handling | 1 | New | 192129.0459 | Total Volume | 1000 | m3
Sludge Tanks, Pre-Fabricated, Circular - Civil | 2F - Sludge Handling | 1 | New | 1223492.6303 | Total Volume | 1500 | m3
Sludge Thickening Beltpresses - M&E | 2F - Sludge Handling | 1 | New | 1142993.7548 | Sludge Production | 15000 | TDS/year
Sludge Tanks, Pre-Fabricated, Circular - Civil <#2> | 2G - Sludge Centre | 1 | New | 876052.7313 | Total Volume | 1000 | m3
Thermal Hydrolysis | 2G - Sludge Centre | 1 | New | 12099744.38 | Sludge Production | 23000 | TDS/year
Cake Slab - Civil | 2G - Sludge Centre | 1 | New | 294902.2806 | Surface Area | 480 | m2
Sludge Mixers - M&E <#2> | 2G - Sludge Centre | 1 | New | 192129.0459 | Total Volume | 1000 | m3
Sludge Dewatering Centrifuges - M&E | 2G - Sludge Centre | 1 | New | 3377552.0206 | Sludge Production | 12650 | TDS/year
Digestion | 2G - Sludge Centre | 1 | New | 6548694.7222 | Total Volume | 12600 | m3
Cake Slab - Civil <#2> | 2G - Sludge Centre | 4 | New | 3123828.5864 | Total Volume | 2530 | m3
Ultrasonic Level | CET - Centrate Treatment | 1 | New | 2394.9061 | Quantity | 1 | Number
Temperature Monitor | CET - Centrate Treatment | 1 | New | 1755.8302 | Quantity | 1 | Number
Different. Pres Flow | CET - Centrate Treatment | 5 | New | 16310.4807 | Diameter | 100 | mm
Direct Online Starter | CET - Centrate Treatment | 1 | New | 9792.3396 | Power | 10 | kW
PLC <#2> | CET - Centrate Treatment | 1 | New | 19549.1758 | In/Out cards | 3 | Number
Heat Exchanger | CET - Centrate Treatment | 1 | New | 94477.6601 | Rated Heat Transfer | 200 | kW
Gate Valve | CET - Centrate Treatment | 5 | New | 2905.6482 | Diameter | 100 | mm
Impellor Mixer | CET - Centrate Treatment | 1 | New | 36054.276 | Power | 10 | kW
Rigid Pipework <#5> | CET - Centrate Treatment | 5 | New | 114317 | Diameter | 100 | mm
[5 empty] | Length | 50 | m
Gas Holder | CHP - CHP Plant | 1 | New | 380780.3065 | Total Volume | 2500 | m3
Probes (Level) | CHP - CHP Plant | 4 | New | 7412.9304 | Quantity | 1 | Number
Rigid Pipework <#2> | CHP - CHP Plant | 2 | New | 32949 | Diameter | 700 | mm
[5 empty] | Length | 1.5 | m
Flare Stack | CHP - CHP Plant | 1 | New | 231784.6422 | Height | 5 | m
Screw Compressor <#2> | CHP - CHP Plant | 1 | New | 21863.5052 | Power | 5 | kW
Rigid Pipework <#4> | CHP - CHP Plant | 1 | New | 224454.9927 | Diameter | 350 | mm
[5 empty] | Length | 200 | m
Transformer | ELE - Electrical Distribution | 1 | New | 120745.7192 | Capacity | 2500 | kW
Scada | SBS - Site Services | 1 | New | 72505.5891 | Memory Capacity | 500 | GB
Store | SBS - Site Services | 4 | New | 2076146.6488 | Footprint Area | 2530 | m2
Hardstanding Area | SBS - Site Services | 1 | New | 45569.6151 | Footprint Area | 272 | m2
External Site Lighting | SBS - Site Services | 10 | New | 32988.1288 | Type | Flood Lighting On Columns
External Site Lighting <#2> | SBS - Site Services | 3 | New | 13772.8275 | Type | Street Light
External Site Lighting <#3> | SBS - Site Services | 4 | New | 9955.0883 | Type | Lighting Fixed On Buildings
Gate (Elec) <#2> | SBS - Site Services | 2 | New | 49848.0814 | Width | 4 | m
Footpath | SBS - Site Services | 1 | New | 25035.0526 | Area | 272 | m2
Fan | SBS - Site Services | 1 | New | 13717.1871 | Power | 7.5 | kW
Hardstanding Area <#2> | SBS - Site Services | 1 | New | 6627.2125 | Area | 15 | m2
Chamber | SBS - Site Services | 1 | New | 101080.6304 | Total Volume | 45 | m3
Hydraulic Pack | SLD - Sludge Dewatering | 1 | New | 62830.903 | Power | 12 | kW
Horizontal Sliding Frame | SLD - Sludge Dewatering | 1 | New | 139167.5191 | Floor Frame Area | 36 | m2
Steps | SLD - Sludge Dewatering | 1 | New | 13539.5079 | Height | 3 | m
Steps <#2> | SLD - Sludge Dewatering | 1 | New | 23158.5764 | Height | 5 | m
PLC <#3> | SLD - Sludge Dewatering | 1 | New | 44604.9488 | In/Out cards | 12 | Number
Screw/Auger Conveyor | SLD - Sludge Dewatering | 2 | New | 70185.6498 | Screw Diameter | 250 | mm
Screw/Auger Conveyor <#2> | SLD - Sludge Dewatering | 4 | New | 140371.2996 | Screw Diameter | 250 | mm
Odour Control | SS - Site Services | 1 | New | 1080995.4546 | Air Flow | 7000 | m3/hr
Kiosks | SS - Site Services | 1 | New | 95071.87 | Area | 36 | m2
Site Security CCTV | SS - Site Services | 1 | New | 138434.3898 | Number of Camera | 12 | Number
Buildings | SS - Site Services | 1 | New | 293551.3292 | Footprint Area | 128 | m2
Roads | SS - Site Services | 2 | New | 454410.6376 | Area | 2000 | m2
Landscaping | SS - Site Services | 1 | New | 40747.4423 | Area | 1000 | m2
Washwater Pumping Stations | SS - Site Services | 1 | New | 378731.3318 | Total Installed Power | 33 | kW
Washwater Pressure Pipelines | SS - Site Services | 1 | New | 72362.8383 | Length | 500 | m
Boundary Fencing | SS - Site Services | 1 | New | 168806.2441 | Length | 950 | m
Buildings <#2> | SS - Site Services | 1 | New | 405210.4114 | Footprint Area | 190 | m2
Buildings <#3> | SS - Site Services | 1 | New | 531277.1171 | Footprint Area | 260 | m2
Buildings <#4> | SS - Site Services | 1 | New | 693362.8816 | Footprint Area | 350 | m2
Boundary Fencing <#2> | SS - Site Services | 1 | New | 27424.7414 | Length | 140 | m
Telemetry | SS - Site Services | 1 | New | 68215.2129 | Quantity | 5 | Number
Kiosks <#2> | SS - Site Services | 1 | New | 111066.8262 | Area | 41 | m2
Odour Control <#2> | SS - Site Services | 1 | New | 642191.569 | Air Flow | 3000 | m3/hr
Biodiversity Net Gain | SS - Site Services | 1 | New | 1140000 | Number of Units | 38
Closed Round Tank (Level Floor) | SST - Sludge Storage | 1 | New | 618170.8973 | Total Volume | 1000 | m3
Rigid Pipework <#6> | TSS - Treated Sludge Storage | 1 | New | 34619.92 | Diameter | 200 | mm
[5 empty] | Length | 40 | m
Rigid Pipework <#7> | TSS - Treated Sludge Storage | 1 | New | 34619.92 | Diameter | 200 | mm
[5 empty] | Length | 40 | m
Barrier | TSS - Treated Sludge Storage | 1 | New | 9298.4389 | Length | 3000 | mm
Fixed Gas Monitor | TSS - Treated Sludge Storage | 1 | New | 4843.7122 | Quantity | 1 | Number
Closed Round Tank (Conical Floor) | TWR - Tanker Waste Reception | 1 | New | 266756.5527 | Total Volume | 200 | m3
Walkway | TWR - Tanker Waste Reception | 1 | New | 95756.3467 | Area | 400 | m2
Handrail | TWR - Tanker Waste Reception | 1 | New | 7548.5244 | Length | 22 | m
Ladder | TWR - Tanker Waste Reception | 1 | New | 2752.4196 | Height | 3 | m
Platform | TWR - Tanker Waste Reception | 1 | New | 74474.4278 | Area | 29.25 | m
Induction (LV) | TWR - Tanker Waste Reception | 2 | New | 23116.3973 | Power | 15 | kW
Star Delta Starter | TWR - Tanker Waste Reception | 2 | New | 27611.465 | Power | 15 | kW
Helical Rotor (Progressive Cavity) | TWR - Tanker Waste Reception | 2 | New | 42299.0839 | Pump Rating | 15 | kW
Strainpress | TWR - Tanker Waste Reception | 2 | New | 241379.2822 | Capacity | 33 | l/s
Total Asset direct costs |  |  |  | 46279054.2416
EPR Permit Application |  |  |  | 40000
Site Wide Electrical Distibution |  |  |  | 2663345.62
Location Factors
| Does the site have poor ground conditions - does it need piling? |  |  | 1312728.3163
| Does the solution require an extensive planning effort? |  |  | 283800.8708
| Does the statutory power supply need upgrading? |  |  | 192674.9111
| Is an Environmental Impact Assessment (EIA) report required? |  |  | 1028630.3971
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 659040.2882
Total Location Factor Costs |  |  |  | 3476874.7834
On Cost |  |  |  | 16199788.76
Grand Total |  |  |  | 68659063.405

## Resilience (water)
Investment Code | I010479 |  |  |  |  | the cost show are total costs including Labour, Plant, materials and prelims, Location factors and On costs
Investment Title | Bramford no.1 Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Platform | BRM1WA-1A-BOR | 1 | New | 30800.1288 | Area | 11.5 | m2
Steps | BRM1WA-1A-BOR | 1 | New | 3920.4395 | Height | 1 | m
Cabling Ducting | BRM1WA-1A-BOR | 1 | New | 6881.7793 | Length (m) | 10 | m
Rigid Pipework | BRM1WA-1A-BOR | 1 | New | 12249.9472 | Diameter (mm) | 610 | mm
[5 empty] | Length | 3 | m
B/H Rising Main 1 Borehole Pump 1 | BRAMWW-1A-BOR-PS01-BHR001 | 1 | Replacement | 7193.448 | Length (m) | 6.12 | m
[5 empty] | Diameter (mm) | 250 | mm
Borehole Pump 1 | BRAMWW-1A-BOR-PS01-BHP001 | 1 | Replacement | 36173.3629 | Pump Rating (kW) | 140 | kW
Air Release Valve | BRM1WA-1A-BOR | 1 | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
Air Release Valve 1 Borehole Pump 1 | BRAMWW-1A-BOR-PS01-ARV001 | 1 | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
Non Return Valve 1 Borehole Pump 1 | BRAMWW-1A-BOR-PS01-NRV001 | 1 | Replacement | 5707.6171 | Nominal Bore (mm) | 250 | mm
Sample Tap | BRM1WA-1A-BOR | 1 | Replacement | 10841.9551 | qty | 1 | unit
Starter Panel - BH Pump 1 | BRAMWW-1A-BOR-PS01-STA001 | 1 | Refurbishment | 7901.4813 | Installed Power (kW) | 140 | kW
Level Monitor 1 Borehole | BRAMWW-1A-BOR-PS01-LEV001 | 1 | Replacement | 4702.8966 | qty | 1 | unit
Borehole Headplate | BRM1WA-1A-BOR | 1 | Replacement | 10813.4096 | Borehole Diameter (mm) | 750 | mm
Kiosks | BRM1WA-SS | 1 | New | 87877.932 | Area | 25 | m2
| Total Asset direct costs |  |  | 226792.7286
Total Location Factor Costs
| On Cost |  |  | 105914.7671
| Grand Total |  |  | 332707.4957
Investment Code | I010481
Investment Title | Bramford no.2 Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Platform | AW_W_NI-1A-BOR | 1 | New | 30800.1288 | Area | 11.5 | m2
Steps | BRM2WA-1A-BOR | 1 | New | 3920.4395 | Height | 1 | m
Cabling Ducting | AW_W_NI-1A-BOR | 1 | New | 1846.9388 | Length (m) | 10 | m
Rigid Pipework | AW_W_NI-1A-BOR | 1 | New | 12249.9472 | Diameter (mm) | 610 | mm
[5 empty] | Length | 3 | m
B/H Rising Main 1 Borehole Pump 1 | BRAMWW-1A-BOR-PS01-BHR001 | 1 | Replacement | 7193.448 | Length (m) | 6.12 | m
[5 empty] | Diameter (mm) | 250 | mm
Air Release Valve | AW_W_NI-1A-BOR | 1 | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
Air Release Valve 1 Borehole Pump 1 | BRAMWW-1A-BOR-PS01-ARV001 | 1 | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
Non Return Valve 1 Borehole Pump 1 | BRAMWW-1A-BOR-PS01-NRV001 | 1 | Replacement | 5707.6171 | Nominal Bore (mm) | 250 | mm
Probes (Level) | AW_W_NI-1A-BOR | 1 | Replacement | 2930.4177 | qty | 1 | each
Magflow | AW_W_NI-1A-BOR | 1 | Replacement | 6373.4199 | Diameter (mm) | 250 | mm
Level Monitor 1 Borehole | BRAMWW-1A-BOR-PS01-LEV001 | 1 | Replacement | 4702.8966 | qty | 1 | unit
Borehole Headplate | BRM2WA-1A-BOR | 1 | Replacement | 10813.4096 | Borehole Diameter (mm) | 750 | mm
Kiosks -LPBC3 | BRM1WA-SS | 1 | New | 40907.8833 | Area | 11.2 | m2
| Total Asset direct costs |  |  | 129174.8777
| Site wide Electrical Distribution |  |  | 7427.5555
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 9299.1108
| Total Location Factor Costs |  |  | 16726.6662
| On Cost |  |  | 69473.0433
| Grand Total |  |  | 215374.5872
Investment Code | I010494
Investment Title | Westerfield BH 2 Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Cabling Ducting | AW_W_NI-1A-BOR | 1 | New | 1846.9388 | Length (m) | 10 | m
BH Rising Main - BH Pump 2 | WESTBS-1A-BOR-PS02-BHR002 |  | Replacement | 5877 | Length (m) | 5 | m
[5 empty] | Diameter (mm) | 250 | mm
Rigid Pipework | AW_W_NI-1A-BOR | 1 | New | 6941.6367 | Diameter (mm) | 610 | mm
[5 empty] | Length | 1.7 | m
Air Release Valve - BH Pump 2 | WESTBS-1A-BOR-PS02-ARV002 |  | Replacement | 929.7853 | Nominal Bore (mm) | 30 | mm
[5 empty] | Length |  | m
Air Release Valve | AW_W_NI-1A-BOR | 1 | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
Check Valve | AW_W_NI-1A-BOR | 1 | Replacement | 5873.8717 | Nominal Bore (mm) | 250 | mm
Sample Tap | AW_W_NI-1A-BOR | 1 | Replacement | 10841.9551 | qty | 1 | unit
Non Return Valve - BH Pump 2 | WESTBS-1A-BOR-PS02-NRV002 |  | Replacement | 8130.7178 | Nominal Bore (mm) | 250 | mm
Probes (Level) | WES2WA-1A-BOR | 1 | Replacement | 2930.4177 | qty | 1 | unit
Magflow | AW_W_NI-1A-BOR | 1 | Replacement | 6373.4199 | Diameter (mm) | 250 | mm
Pressure Monitor | WES2WA-1A-BOR | 1 | Replacement | 2479.2044 | qty | 1 | unit
Pressure Gauge | WES2WA-1A-BOR | 1 | Replacement | 1473.82 | qty | 1 | unit
Borehole Headplate | WES2WA-1A-BOR | 1 | Replacement | 10813.4096 | Borehole Diameter (mm) | 750 | mm
Borehole Backfill | BOR - Borehole Abstraction | 1 | Refurbishment | 9746.2051 | Borehole Volume | 31 | m3
[5 empty] | Depth (m) | 110 | m
| Total Asset direct costs |  |  | 75122.5477
Location
| Site wide Electrical Distribution |  |  | 4319.5465
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 7361.7435
| Total Location Factor Costs |  |  | 11681.29
| On Cost |  |  | 42288.1109
| Grand Total |  |  | 129091.9486
Investment Code | I010498
Investment Title | West Bradenham 2 Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Platform | WBD2WA-1A-BOR | 1 | New | 11344.1494 | Area | 4 | m2
Steps | WBD2WA-1A-BOR | 1 | New | 3920.4395 | Height | 1 | m
Cabling Ducting | AW_W_NI-1A-BOR | 1 | New | 1846.9388 | Length (m) | 10 | m
Rigid Pipework | AW_W_NI-1A-BOR | 1 | New | 4083.3157 | Diameter (mm) | 610 | mm
[5 empty] | Length | 1 | m
BH Rising Main - H Pump 2 P2/01 | WBRNWW-1A-BOR-PS01-BHR001 |  | New | 5877 | Length (m) | 5 | m
[5 empty] | Diameter (mm) | 250 | mm
Air Release Valve | AW_W_NI-1A-BOR | 1 | Replacement | 929.7853 | Nominal Bore (mm) | 30 | mm
Air Release Valve - Bh Pump 2 | WBRNWW-1A-BOR-PS01-ARV001 |  | Replacement | 929.7853 | Nominal Bore (mm) | 30 | mm
Process Valve - BH Pump 2 P2/01 | WBRNWW-1A-BOR-PS01-PCV001 |  | Replacement | 684.8718 | Nominal Bore (mm) | 150 | mm
Sample Tap | AW_W_NI-1A-BOR | 1 | Replacement | 10841.9551 | qty | 1 | unit
Non Return Valve - BH Pump 2 P2/01 | WBRNWW-1A-BOR-PS01-NRV001 |  | Replacement | 8130.7178 | Nominal Bore (mm) | 250 | mm
Probes (Level) | AW_W_NI-1A-BOR | 1 | Replacement | 2930.4177 | qty | 1 | each
Flow Switch | AW_W_NI-1A-BOR | 1 | Replacement | 1045.5518 | qty | 1 | unit
Flow Switch <#2> | AW_W_NI-1A-BOR | 1 | Replacement | 1045.5518 | qty | 1 | unit
Magflow | AW_W_NI-1A-BOR | 1 | Replacement | 6373.4199 | Diameter (mm) | 250 | mm
Level Monitor - Borehole 2 | WBRNWW-1A-BOR-PS01-LEV001 |  | Replacement | 2479.2044 | qty | 1 | unit
Pressure Monitor - Borehole Pmp 2 (2/01) | WBRNWW-1A-BOR-PS01-PRE001 |  | Replacement | 1473.82 | qty | 1 | unit
Borehole Headplate | WBD2WA-1A-BOR | 1 | Replacement | 10813.4096 | Borehole Diameter (mm) | 750 | mm
| Total Asset direct costs |  |  | 74750.334
| Site wide Electrical Distribution |  |  | 4298.1442
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 7346.0003
| Total Location Factor Costs |  |  | 11644.1445
| On Cost |  |  | 42097.4389
| Grand Total |  |  | 128491.9174
Investment Code | I010504
Investment Title | Wellington A Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Platform | AW_W_NI-1A-RAB | 1 | New | 30800.1288 | Area | 11.5 | m2
Steps | MTHABS-1A-BOR | 1 | New | 3920.4395 | Height | 1 | m
Kiosk | AW_W_NI-SS-SBS | 1 | New | 34219.4879 | Length (m) | 11.2 | m
Rigid Pipework | AW_W_NI-1A-BOR | 1 | New | 20474.9357 | Diameter (mm) | 915 | mm
[5 empty] | Length | 2 | m
B/H Rising Main 1 Borehole Pump 1 | MTHABS-1A-BOR-PS01-BHR001 | 1 | Replacement | 5877 | Length (m) | 5 | m
[5 empty] | Diameter (mm) | 203 | mm
Air Release Valve 1 Borehole Pump 1 | MTHABS-1A-BOR-PS01-ARV001 | 1 | Replacement | 929.7853 | Nominal Bore (mm) | 30 | mm
MTHABS-1A-BOR-PV01-NRV | MTHABS-1A-BOR-PV01-NRV | 1 | Replacement | 5873.8717 | Nominal Bore (mm) | 250 | mm
Sample Tap | AW_W_NI-1A-RAB | 1 | Replacement | 10841.9551 | qty | 1 | unit
Non Return Valve 1 Borehole Pump 1 | MTHABS-1A-BOR-PS01-NRV001 | 1 | Replacement | 8130.7178 | Nominal Bore (mm) | 250 | mm
Probes (Level) | AW_W_NI-1A-BOR | 1 | Replacement | 2930.4177 | qty | 1 | unit
Level Controller - Borehole Low Level | MTHABS-1A-BOR-PC01-LEC001 | 1 | Replacement | 2930.4177 | qty | 1 | unit
Flow Switch | AW_W_NI-1A-BOR | 1 | Replacement | 1045.5518 | qty | 1 | unit
Lars Flowmeter 1 | MTHABS-1A-BOR-PM01-LAR002 | 1 | Replacement | 3545.9244 | Diameter (mm) | 150 | mm
Level Monitor 2 Borehole Depth | MTHABS-1A-BOR-PS01-LEV002 | 1 | Replacement | 2479.2044 | qty | 1 | unit
Pressure Gauge | MTHABS-1A-BOR | 1 | Replacement | 1473.82 | qty | 1 | unit
Borehole Headplate | MTHABS-1A-BOR | 1 | Replacement | 12273.133 | Borehole Diameter (mm) | 1000 | mm
| Total Asset direct costs |  |  | 147746.7908
| Site wide Electrical Distribution |  |  | 8495.4405
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 9853.3965
| Total Location Factor Costs |  |  | 18348.837
| On Cost |  |  | 78638.9146
| Grand Total |  |  | 244734.5424
Investment Code | I018463
Investment Title | Swaton no.1 Borehole Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Flap Valve | SWA1WA-1A-BOR | 1 | New | 748.479 | Nominal Bore (mm) | 100 | mm
Borehole Backfill | SWA1WA-1A-BOR | 3 | Refurbishment | 30072.1029 | Borehole Volume | 33 | m3
[5 empty] | Depth (m) | 94.5 | m
Water Main <#2> | AW_W_I | 1 | New | 10588.5603 | Nominal Bore (mm) | 100 | mm
[5 empty] | Depth (mm) | 900 | mm
[5 empty] | Length in Field (m) | 75 | m
Water Main | AW_W_I | 1 |  | 47704.0656 | Nominal Bore (mm) | 100 | mm
[5 empty] | Depth (mm) | 900 | mm
[5 empty] | Length in Field (m) | 150 | m
[5 empty] | Length in Type 3/4 Reinstatement (m) | 100 | m
Kiosks LPBC4 | SWA1WA-SS | 1 | New | 151132.7098 | Area (m2) | 25 | m2
Roads | SWA1WA-SS | 1 |  | 50819.3713 | Area (m2) | 352 | m2
Boundary Fencing | SWA1WA-SS | 1 | New | 94696.6856 | Length (m) | 100 | m
Landscaping | SWA1WA-SS | 1 |  | 4403.8978 | Area (m2) | 40 | m2
Number of telemetry outstations | SWA1WA-SS | 1 |  | 13643.0426 | Number of Telemetry Outstations | 1 | unit
Fire Alarm Cntrl Pan | BLD - BUILDING | 1 | New | 7146.9349 | Building floor area protected | 25 | m2
Fixed Fire Suppression Cylinder | SBS - Site Services | 1 | New | 14392.8147 | Number of cylinders | 2 | each
Gate (Mech) | SBS - Site Services | 1 | New | 7753.4934 | Width (m) | 3 | m
[5 empty] | Height (mm) | 3000 | mm
Biodiversity Net Gain | SS - Site Services | 1 | New | 26400 | Biodiversity Units | 0.88 | unit
Borehole Shafts | 1A - Abstraction | 1 | New | 249956.3363 | Shaft Depth (m) | 94.5 | m
Borehole Pumps | 1A - Abstraction | 1 | New | 434604 | Total Installed Power (inc standby) (kW) | 66 | kW
| Total Asset direct costs |  |  | 1144062.4943
| Site wide Electrical Distribution |  |  | 65783.5934
| Are access amendments required at the site to enable the works to be carried out? |  |  | 21525.4925
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 20497.3565
| Does the statutory power supply need upgrading? |  |  | 101213.6216
| Is an Environmental Impact Assessment (EIA) report required? |  |  | 25406.7678
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 23807.5946
| Total Location Factor Costs |  |  | 258234.4264
| On Cost |  |  | 604441.246
| Grand Total |  |  | 2006738.1667
Investment Code | I019070
Investment Title | Beck Row Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Platform | AW_W_NI-1A-BOR | 1 | New | 11344.1494 | Area (m2) | 4 | m2
Steps | BECKWW-1A-BOR | 1 | New | 3920.4395 | Height (m) | 1 | m
Cabling Ducting | AW_W_NI-1A-BOR | 1 | New | 1846.9388 | Length (m) | 10 | m
BECKWW-1A-BOR-PS01-BHR01 | BECKWW-1A-BOR-PS01-BHR?01 | 1 | Replacement | 26768.25 | Length (m) | 45 | m
[5 empty] | Diameter (mm) | 150 | mm
Rigid Pipework | AW_W_NI-1A-BOR | 1 | New | 6941.6367 | Length (m) | 1.7 | m
[5 empty] | Diameter (mm) | 610 | mm
Air Release Valve | AW_W_NI-1A-BOR | 1 | Replacement | 929.7853 | Nominal Bore (mm) | 30 | mm
Check Valve | AW_W_NI-1A-BOR | 1 | Replacement | 5873.8717 | Nominal Bore (mm) | 250 | mm
Process Valve 1 Borehole Pump 1 | BECKWW-1A-BOR-PS01-PCV001 |  | Replacement | 3044.636 | Nominal Bore (mm) | 150 | mm
Non Return Valve 1 Borehole Pump 1 | BECKWW-1A-BOR-PS01-NRV001 |  | Replacement | 5707.6171 | Nominal Bore (mm) | 250 | mm
Sample Tap | AW_W_NI-1A-BOR | 1 | Replacement | 10841.9551 | qty | 1 | unit
Probes (Level) | AW_W_NI-1A-BOR | 1 | Replacement | 2930.4177 | qty | 1 | unit
Flow Switch | AW_W_NI-1A-BOR | 1 | Replacement | 1045.5518 | qty | 1 | unit
Magflow | AW_W_NI-1A-BOR | 1 | Replacement | 6373.4199 | Diameter (mm) | 250 | mm
Pressure Monitor | AW_W_NI-1A-BOR | 1 | Replacement | 2479.2044 | qty | 1 | unit
Pressure Gauge | AW_W_NI-1A-BOR | 1 | Replacement | 1473.82 | qty | 1 | unit
Borehole Headplate | BECKWW-1A-BOR | 1 | Replacement | 10813.4096 | Borehole Diameter (mm) | 750 | mm
| Total Asset direct costs |  |  | 102335.1031
| Site wide Electrical Distribution |  |  | 5884.2684
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 8410.9353
| Large Building Refurbishments (150-2000m2 Footprint) |  |  | 15343.7439
| Total Location Factor Costs |  |  | 29638.9476
| On Cost |  |  | 63119.2924
| Grand Total |  |  | 195093.3432
Investment Code | I023214
Investment Title | Denton Lodge Borehole Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Steps | BOR - Borehole Abstraction | 1 | New | 3920.4395 | Height (m) | 1 | m
Rigid Pipework | BOR - Borehole Abstraction | 1 | New | 594.85 | Length (m) | 1 | m
[5 empty] | Diameter (mm) | 150 | mm
Probes (Level) | BOR - Borehole Abstraction | 1 | New | 1853.2326 | qty | 1 | unit
Platform | BOR - Borehole Abstraction | 1 | New | 29532.0557 | Area | 11 | m2
Magflow | BOR - Borehole Abstraction | 1 | New | 6373.4199 | Diameter (mm) | 250 | mm
Ultrasonic Level | BOR - Borehole Abstraction | 1 | New | 2394.9061 | qty | 1 | unit
Kiosks | SS - Site Services | 1 | New | 151132.7098 | Area | 25 | m2
Cabling Ducting | BOR - Borehole Abstraction | 1 | New | 1846.9388 | Length (m) | 10 | m
Borehole Headplate | BOR - Borehole Abstraction | 1 | New | 12273.133 | Borehole Diameter (mm) | 1000 | mm
Rigid Pipework <#2> | BOR - Borehole Abstraction | 1 | New | 2529.6445 | Length (m) | 1 | m
[5 empty] | Diameter (mm) | 533 | mm
Air Release Valve | BOR - Borehole Abstraction | 1 | New | 613.8232 | Nominal Bore (mm) | 25 | mm
Air Release Valve <#2> | BOR - Borehole Abstraction | 1 | New | 613.8232 | Nominal Bore (mm) | 25 | mm
| Total Asset direct costs |  |  | 213678.9763
| Site wide Electrical Distribution |  |  | 12286.5411
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 11551.8359
| Total Location Factor Costs |  |  | 23838.377
| On Cost |  |  | 110698.0119
| Grand Total |  |  | 348215.3652
Investment Code | I040210
Investment Title | CV Regional Overheating Protection RW
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Vent | BLD - BUILDING | 20 | New | 87526.3501 | Vent Area (m2) | 2 | m2
[5 empty] | Installed Power (kW) | 3 | kW
Fan | SBS - Site Services | 20 | New | 170951.9751 | Installed Power (kW) | 3 | kW
PLC | SBS - Site Services | 20 | New | 390983.5151 | In/Out Cards (number) | 3 | each
Direct Online Starter | SBS - Site Services | 20 | New | 136089.0006 | Installed Power (kW) | 3 | kW
Temperature Switch | SBS - Site Services | 20 | New | 15278.265 | qty | 20 | each
Temperature Monitor | SBS - Site Services | 20 | New | 35116.6049 | qty | 20 | each
| Total Asset direct costs |  |  | 835945.7106
| Site wide Electrical Distribution |  |  | 48066.8784
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 22663.8846
| Total Location Factor Costs |  |  | 70730.763
| On Cost |  |  | 241991.9508
| Grand Total |  |  | 1148668.4244
Investment Code | I040278
Investment Title | CV - Reg Temp Related Asset Failure WTW
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Temperature Monitor | SBS - Site Services | 8 | New | 14046.642 | qty | 8 | each
Temperature Switch | SBS - Site Services | 8 | New | 6111.306 | qty | 8 | each
PLC | SBS - Site Services | 16 | New | 312786.8121 | In/Out Cards (number) | 3 | each
Vent | SBS - Site Services | 16 | New | 58396.8 | Vent Area (m2) | 1 | m2
[5 empty] | Installed Power (kW) | 3 | kW
Fan | BLD - BUILDING | 16 | New | 136761.58 | Installed Power (kW) | 3 | kW
| Total Asset direct costs |  |  | 528103.14
| Site wide Electrical Distribution |  |  | 30365.9306
| Medium Building Refurbishments (30-150m2 Footprint) |  |  | 2489.4446
| Total Location Factor Costs |  |  | 32855.3751
| On Cost |  |  | 149719.8277
| Grand Total |  |  | 710678.3429
Investment Code | I040279
Investment Title | CV - Region Temp Related Asset Failure TWD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Temperature Monitor | SBS - Site Services | 24 | New | 42139.9259 | qty | 8 | each
Temperature Switch | SBS - Site Services | 24 | New | 18333.918 | qty | 8 | each
PLC | SBS - Site Services | 19 | New | 371434.3393 | In/Out Cards (number) | 3 | each
Vent | SBS - Site Services | 24 | New | 87595.2 | Vent Area (m2) | 1 | m2
[5 empty] | Installed Power (kW) | 3 | kW
Fan | BLD - BUILDING | 24 | New | 205142.3701 | Installed Power (kW) | 3 | kW
| Total Asset direct costs |  |  | 724645.7532
| Site wide Electrical Distribution |  |  | 41667.1308
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 19646.3569
| Small Building Refurbishments (1-30m2 Footprint) |  |  | 921.97
| Total Location Factor Costs |  |  | 62235.4576
| On Cost |  |  | 168235.2029
| Grand Total |  |  | 955116.4137
Investment Code | I040459
Investment Title | Hillington Chalk 1 Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Cabling Ducting | AW_W_NI-1A-BOR | 1 | New | 1846.9388 | Length (m) | 10 | m
Rigid Pipework | AW_W_NI-1A-BOR | 1 | New | 6941.6367 | Length (m) | 1.7 | m
[5 empty] | Diameter (mm) | 610 | mm
Air Release Valve | AW_W_NI-1A-BOR | 1 | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
Check Valve | AW_W_NI-1A-BOR | 1 | Replacement | 5873.8717 | Nominal Bore (mm) | 250 | mm
Sample Tap | AW_W_NI-1A-BOR | 1 | Replacement | 10841.9551 | qty | 1 | unit
Magflow | AW_W_NI-1A-BOR | 1 | Replacement | 6373.4199 | Diameter (mm) | 250 | mm
Borehole Headplate | BOR - Borehole Abstraction | 1 | New | 9866.2705 | Borehole Diameter (mm) | 609 | mm
Air Release Valve <#2> | AW_W_NI-1A-BOR | 1 | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
Rigid Pipework <#2> | BOR - Borehole Abstraction | 1 | New | 1998.18 | Length (m) | 1.7 | m
[5 empty] | Diameter (mm) | 400 | mm
Pressure Gauge | BOR - Borehole Abstraction | 1 | New | 783.7147 | qty | 1 | unit
Pressure Monitor | BOR - Borehole Abstraction | 1 | New | 2512.4695 | qty | 1 | unit
Probes (Level) | BOR - Borehole Abstraction | 1 | New | 1853.2326 | qty | 1 | unit
Borehole Backfill | BOR - Borehole Abstraction | 1 | Refurbishment | 5481.971 | Borehole Volume | 8.62 | m3
[5 empty] | Depth (m) | 30.5 | m
| Total Asset direct costs |  |  | 56101.9918
| Site wide Electrical Distribution |  |  | 3225.8645
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 6491.3244
| Total Location Factor Costs |  |  | 9717.189
| On Cost |  |  | 32457.8713
| Grand Total |  |  | 98277.0521
Investment Code | I040461
Investment Title | Hillington Chalk 2 Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Cabling Ducting | AW_W_NI-1A-BOR | 1 | New | 1846.9388 | Length (m) | 10 | m
Rigid Pipework | AW_W_NI-1A-BOR | 1 | New | 6941.6367 | Length (m) | 1.7 | m
[5 empty] | Diameter (mm) | 610 | mm
Air Release Valve | AW_W_NI-1A-BOR | 1 | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
Check Valve | AW_W_NI-1A-BOR | 1 | Replacement | 5873.8717 | Nominal Bore (mm) | 250 | mm
Sample Tap | AW_W_NI-1A-BOR | 1 | Replacement | 10841.9551 | qty | 1 | unit
Magflow | AW_W_NI-1A-BOR | 1 | Replacement | 6373.4199 | Diameter (mm) | 250 | mm
Borehole Headplate | BOR - Borehole Abstraction | 1 | New | 9866.2705 | Borehole Diameter (mm) | 609 | mm
Air Release Valve <#2> | AW_W_NI-1A-BOR | 1 | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
Rigid Pipework <#2> | BOR - Borehole Abstraction | 1 | New | 1998.18 | Length (m) | 1.7 | m
[5 empty] | Diameter (mm) | 400 | mm
Pressure Gauge | BOR - Borehole Abstraction | 1 | New | 783.7147 | qty | 1 | unit
Pressure Monitor | BOR - Borehole Abstraction | 1 | New | 2512.4695 | qty | 1 | unit
Probes (Level) | BOR - Borehole Abstraction | 1 | New | 1853.2326 | qty | 1 | unit
Kiosks-LPBC4 | SS - Site Services | 1 | New | 78281.1512 | Area (m2) | 11.5 | m2
| Total Asset direct costs |  |  | 128901.172
| Site wide Electrical Distribution |  |  | 7411.8174
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 9290.6134
| Total Location Factor Costs |  |  | 16702.4307
| On Cost |  |  | 69337.4105
| Grand Total |  |  | 214941.0133
Investment Code | I040474
Investment Title | Southfields Bore 2 Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Borehole Backfill <#2> | SS - Site Services | 2 | Refurbishment | 16081.8645 | Borehole Volume | 20.21 | m3
[5 empty] | Depth | 16 | m3
Total Asset direct costs
Site wide Electrical Distribution
Is existing site demolition / enabling works required to allow the solutions to be realised?
Total Location Factor Costs
| On Cost |  |  | 8437.8668
| Grand Total |  |  | 24519.7313
Investment Code | I040759
Investment Title | Wellington Plantation B Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Platform | AW_W_NI-1A-RAB | 1 | New | 30800.1288 | Area | 11.5 | m2
Steps | MTHABS-1A-BOR | 1 | New | 3920.4395 | Height | 1 | m2
Kiosk | AW_W_NI-SS-SBS | 1 | New | 34219.4879 | Footprint Area (m2) | 11.2 | m2
Rigid Pipework | AW_W_NI-1A-BOR | 1 | New | 20474.9357 | Length (m) | 2 | m2
[5 empty] | Diameter (mm) | 915 | mm
B/H Rising Main 1 Borehole Pump 1 | MTHABS-1A-BOR-PS01-BHR001 |  | Replacement | 5877 | Length (m) | 5 | m2
[5 empty] | Diameter (mm) | 203 | mm
Air Release Valve 1 Borehole Pump 1 | MTHABS-1A-BOR-PS01-ARV001 |  | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
MTHABS-1A-BOR-PV01-NRV??? | MTHABS-1A-BOR-PV01-NRV??? |  | Replacement | 5873.8717 | Nominal Bore (mm) | 250 | mm
Sample Tap | AW_W_NI-1A-RAB | 1 | Replacement | 10841.9551 | qty | 1 | unit
Non Return Valve 1 Borehole Pump 1 | MTHABS-1A-BOR-PS01-NRV001 |  | Replacement | 8130.7178 | Nominal Bore (mm) | 250 | mm
Probes (Level) | AW_W_NI-1A-BOR | 1 | Replacement | 2930.4177 | qty | 1 | unit
Level Controller - Borehole Low Level | MTHABS-1A-BOR-PC01-LEC001 |  | Replacement | 2930.4177 | qty | 1 | unit
Flow Switch | AW_W_NI-1A-BOR | 1 | Replacement | 1045.5518 | qty | 1 | unit
Lars Flowmeter 1 | MTHABS-1A-BOR-PM01-LAR002 |  | Replacement | 3545.9244 | Diameter (mm) | 150 | mm
Level Monitor 2 Borehole Depth | MTHABS-1A-BOR-PS01-LEV002 |  | Replacement | 2479.2044 | qty | 1 | unit
Pressure Gauge | MTHABS-1A-BOR | 1 | Replacement | 1473.82 | qty | 1 | unit
Borehole Headplate | MTHABS-1A-BOR | 1 | Replacement | 12273.133 | Borehole Diameter (mm) | 1000 | mm
| Total Asset direct costs |  |  | 147681.1711
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 9616.9634
Total Location Factor Costs
| On Cost |  |  | 74652.2335
| Grand Total |  |  | 231950.368
Investment Code | I040761
Investment Title | Wellington Plantation D Flooding
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Platform | AW_W_NI-1A-RAB | 1 | New | 30800.1288 | Area | 11.5 | m2
Steps | MTHABS-1A-BOR | 1 | New | 3920.4395 | Height | 1 | m2
Kiosk | AW_W_NI-SS-SBS | 1 | New | 34219.4879 | Footprint Area (m2) | 11.2 | m2
Rigid Pipework | AW_W_NI-1A-BOR | 1 | New | 20474.9357 | Length (m) | 2 | m2
[5 empty] | Diameter (mm) | 915 | mm
B/H Rising Main 1 Borehole Pump 1 | MTHABS-1A-BOR-PS01-BHR001 |  | Replacement | 5877 | Length (m) | 5 | m2
[5 empty] | Diameter (mm) | 203 | mm
Air Release Valve 1 Borehole Pump 1 | MTHABS-1A-BOR-PS01-ARV001 |  | Replacement | 864.1656 | Nominal Bore (mm) | 25 | mm
MTHABS-1A-BOR-PV01-NRV??? | MTHABS-1A-BOR-PV01-NRV??? |  | Replacement | 5873.8717 | Nominal Bore (mm) | 250 | mm
Sample Tap | AW_W_NI-1A-RAB | 1 | Replacement | 10841.9551 | qty | 1 | unit
Non Return Valve 1 Borehole Pump 1 | MTHABS-1A-BOR-PS01-NRV001 |  | Replacement | 8130.7178 | Nominal Bore (mm) | 250 | mm
Probes (Level) | AW_W_NI-1A-BOR | 1 | Replacement | 2930.4177 | qty | 1 | unit
Level Controller - Borehole Low Level | MTHABS-1A-BOR-PC01-LEC001 |  | Replacement | 2930.4177 | qty | 1 | unit
Flow Switch | AW_W_NI-1A-BOR | 1 | Replacement | 1045.5518 | qty | 1 | unit
Lars Flowmeter 1 | MTHABS-1A-BOR-PM01-LAR002 |  | Replacement | 3545.9244 | Diameter (mm) | 150 | mm
Level Monitor 2 Borehole Depth | MTHABS-1A-BOR-PS01-LEV002 |  | Replacement | 2479.2044 | qty | 1 | unit
Pressure Gauge | MTHABS-1A-BOR | 1 | Replacement | 1473.82 | qty | 1 | unit
Borehole Headplate | MTHABS-1A-BOR | 1 | Replacement | 12273.133 | Borehole Diameter (mm) | 1000 | mm
| Total Asset direct costs |  |  | 147681.1711
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 9616.9634
| Total Location Factor Costs |  |  | 9616.9634
| On Cost |  |  | 74652.2335
| Grand Total |  |  | 231950.368
Investment Code | I028753
Investment Title | NTB18b Bacton 50MLD Supply (d13)
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Water Main | 01 - AW Water Infra | 1 | New | 60362079.32 | Nominal Bore (mm) | 700 | mm
[5 empty] | Depth (mm) | 1200 | mm
[5 empty] | Length in Verge/Unmade (m) | 628 | m
[5 empty] | Length in Field (m) | 27129 | m
[5 empty] | Length in Path (m) | 539 | m
Water Main <#3> | 01 - AW Water Infra | 1 | New | 11085457.9546 | Nominal Bore (mm) | 700 | mm
[5 empty] | Depth (mm) | 5000 | mm
[5 empty] | Length of Microtunnelling (m) | 1134 | m
Telemetry <#2> | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | unit
Standby Generation <#2> | SS - Site Services | 1 | New | 1003009.4196 | Total Installed Power (kW) | 1540 | kW
Landscaping <#2> | SS - Site Services | 1 | New | 17069.911 | Area (m2) | 284 | m2
Roads <#2> | SS - Site Services | 1 | New | 19519.0556 | Area (m2) | 116 | m2
Supply | 1H - Treated Water Pumping | 1 | New | 9387220.2006 | Total Installed Power (inc standby) (kW) | 3080 | kW
Boundary Fencing | SS - Site Services | 1 | New | 22537.4796 | Length (m) | 112 | m
Water Main <#2> | 01 - AW Water Infra | 1 | New | 15665310.98 | Nominal Bore (mm) | 700 | mm
[5 empty] | Length in Type 3/4 Reinstatement (m) | 4642 | m
[5 empty] | Depth (mm) | 1200 | mm
Electricity Meter | ELE - Electrical Distribution | 5 | New | 27340.4086 | qty | 5 | unit
Transformer | ELE - Electrical Distribution | 5 | New | 27170.7575 | Capacity (kW) | 25 | kW
Impressed Current Cath Protection | ELE - Electrical Distribution | 5 | New | 46615.5973 | qty | 5 | unit
Cabling Ducting | ELE - Electrical Distribution | 5 | New | 117693.4651 | Length (m) | 100 | m
Kiosks | SS - Site Services | 5 | New | 47972.588 | Area (m2) | 2 | m2
| Total Asset direct costs |  |  | 97842640.1801
| Site wide Electrical Distribution |  |  | 5625951.8104
| Are the works in a town centre/heavily congested area? |  |  | 6321930.9706
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 1752977.204
| Do the works cross other significant infrastructure - rail lines, open water, major roads, medium and high pressure gas lines? |  |  | 469436.8212
| Does the site have a high water table - does it need dewatering? |  |  | 5222708.8629
| Does the site have poor ground conditions - does it need piling? |  |  | 2772958.2653
| Does the solution need modelling prior to delivery? |  |  | 286370.7289
| Does the solution require an extensive planning effort? |  |  | 125868.0858
| Does the solution require environmental mitigation measures to be implemented? |  |  | 234457.637
| Is an Environmental Impact Assessment (EIA) report required? |  |  | 2172840.4318
| Total Location Factor Costs |  |  | 24985500.8179
| On Cost |  |  | 38549890.3472
| Grand Total |  |  | 161378031.3451
Investment Code | I040214
Investment Title | Raw Water Monitoring
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Condition Monitoring | 01 - AW Water Infra | 336 | New | 737019.36 | qty | 336 | unit
Condition Monitoring <#2> | 01 - AW Water Infra | 167 | New | 633551.24 | qty | 167 | unit
| Total Asset direct costs |  |  | 1370570.6
Total Location Factor Costs
| On Cost |  |  | 213286.6898
| Grand Total |  |  | 1583857.2898

## Resillience (water recycling)
Investment Code | I044082 | [6 empty] | the cost show are total costs including Labour, Plant, materials and prelims, Location factors and On costs
Investment Title | AMP 8 Anwick WRC Flood Prevention Resilience
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Flood Wall (including coastal defence) | SBS - Site Services | 1 | New | 556017.4034 | Wall Length | 531 | m
[5 empty] | Wall Height | 1 | m
Flood gates | SBS - Site Services | 1 | New | 37740.1627 | Gate Height | 1 | m
[5 empty] | Gate Width | 4 | m
Walkway | SBS - Site Services | 1 | New | 82777.02 | Area | 340 | m2
Final Effluent Pumping Station | 2K - Effluent Disposal | 1 | New | 348304.27 | Total Installed Power (inc standby) (kW) | 47 | kW
Rigid Pipework | SBS - Site Services | 1 | New | 52108.5281 | Usage | Rising Main Pipework
[5 empty] | Length | 50 | m
[5 empty] | Diameter | 300 | mm
Biodiversity Net Gain | SS - Site Services | 1 | New | 4200 | Units | 0.14 | Number
Landscaping | SS - Site Services | 1 | New | 8296.5083 | Area | 100 | m2
Telemetry Outstation | TEL - Telemetry | 1 | New | 5122.35 | Type | MM4
| Total Asset direct costs |  |  | 1094566.2425
| Site Wide Electrical Distribution |  |  | 62937.56
| Are access amendments required at the site to enable the works to be carried out? |  |  | 11844.73
| Are specialist scaffolding resources required to access assets? |  |  | 32588.4
| Are temporary works required to keep the existing plant operational? |  |  | 80079.23
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 16432.77
| Does the site have a high water table - does it need dewatering? |  |  | 23732.11
| Does the solution need modelling prior to delivery? |  |  | 2344.96
| Does the solution require an extensive planning effort? |  |  | 6706.5
| Does the statutory power supply need upgrading? |  |  | 38817.83
| Total Location Factor Costs |  |  | 212546.53
| On Cost |  |  | 436414.52
| Grand Total |  |  | 1806464.8525
Investment Code | I044083
Investment Title | AMP 8 Norton Flood Prevention
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Flood Wall (including coastal defence) | SBS - Site Services | 1 | New | 231649.4118 | Wall Length | 200 | m
[5 empty] | Wall Height | 1 | m
Flood gates | SBS - Site Services | 1 | New | 25926.7523 | Gate Height | 1 | m
[5 empty] | Gate Width | 3 | m
Walkway | SBS - Site Services | 1 | New | 52491.9243 | Area | 200 | m2
Final Effluent Pumping Station | 2K - Effluent Disposal | 1 | New | 348304.27 | Total Installed Power (inc standby) (kW) | 47 | kW
Rigid Pipework | SBS - Site Services | 1 | New | 52108.5281 | Usage | Rising Main Pipework
[5 empty] | Length | 50 | m
[5 empty] | Diameter | 300 | mm
Biodiversity Net Gain | SS - Site Services | 1 | New | 4200 | Units | 0.14 | Number
Landscaping | SS - Site Services | 1 | New | 8296.5083 | Area | 100 | m2
Telemetry Outstation | TEL - Telemetry | 1 | New | 5122.35 | Type | MM4
| Total Asset direct costs |  |  | 728099.7449
| Site Wide Electrical Distribution |  |  | 41865.74
| Are access amendments required at the site to enable the works to be carried out? |  |  | 9199.27
| Are specialist scaffolding resources required to access assets? |  |  | 21677.63
| Are temporary works required to keep the existing plant operational? |  |  | 53268.28
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 10930.99
| Does the site have a high water table - does it need dewatering? |  |  | 17281.86
| Does the solution need modelling prior to delivery? |  |  | 1559.85
| Does the solution require an extensive planning effort? |  |  | 4461.13
| Does the statutory power supply need upgrading? |  |  | 25821.42
| Total Location Factor Costs |  |  | 144200.43
| On Cost |  |  | 293207.31
| Grand Total |  |  | 1207373.2249
Investment Code | I044006
Investment Title | Offord Cluny station lane CSO storage resilience
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Collection Storage - Offline | 03 - AW Water Recycling Infra | 1 | New | 364071.89 | Volume of Storage | 100 | m3
[5 empty] | Fencing | 48 | m
[5 empty] | Landscaping | 144 | m2
[5 empty] | Telemetry | 1 | Unit
[5 empty] | Road | 50 | m2
Sewer - Rising Main | 03 - AW Water Recycling Infra | 1 | New | 20869.05 | Length in Verge | 25 | m
[5 empty] | Length in Road type 3/4 | 25 | m
[5 empty] | Diameter | 150 | mm
Sewer - Gravity | 03 - AW Water Recycling Infra | 1 | New | 26297.85 | Length in Road Tpye 3/4 | 25 | m
[5 empty] | Length in Verge | 25 | m
[5 empty] | Depth | 2 | m
[5 empty] | Diameter | 150 | mm
| Total Asset direct costs |  |  | 411238.79
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 3897.9
| Does the solution need modelling prior to delivery? |  |  | 2949.59
| Total Location Factor Costs |  |  | 6847.49
| On Cost |  |  | 200509.3
| Grand Total |  |  | 618595.58
Investment Code | I043663
Investment Title | Roydon Reinstate Village Pond Resilience
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Chamber | NFERSC | 1 | New | 7268.52 | Volume | 1 | m3
Sustainable drainage systems (SuDs) | STALSC | 1 | New | 41305.9 | Volume of Pond | 150 | m3
Sewer - Gravity | STALSC | 1 | New | 20625.05 | Length in Grassland | 40 | m
[5 empty] | Length in Road Type 3/4 | 10 | m
[5 empty] | Depth | 1.5 | m
[5 empty] | Diameter | 150 | mm
| Total Asset direct costs |  |  | 69199.47
| On Cost |  |  | 17562.82
| Grand Total |  |  | 86762.29
Investment Code | I043665
Investment Title | Grimston Land Drainage
| Adjustment | £3,500 per hectare. 5 hectares at Grimston and 5 hectares as Roydon |  | 35000
| Grand Total |  |  | 35000
Investment Code | I044005
Investment Title | AMP8 Tempsford SWM Resilience
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Sewer Laterals | NFERSC | 100 | New | 522517.5781 | Quantity | 1 | Number
Sustainable drainage systems (SuDs) <#4> | STALSC | 1 | New | 87961.704 | Volume of downpipe disconnection | 4 | m3
[5 empty] | Number of properties disconnected | 100 | Number
Sustainable drainage systems (SuDs) | STALSC | 2 | New | 57115.8 | Volume of Pond | 100 | m3
[5 empty] | Volume of Wetland | 100 | m3
Sewer - Gravity | STALSC | 1 | New | 509570.382 | Length in Grassland | 1500 | m
[5 empty] | Depth | 1 | m
[5 empty] | Diameter | 100 | mm
| Total Asset direct costs |  |  | 1177165.4641
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 9700.94
| Does the solution need modelling prior to delivery? |  |  | 8443.17
| Does the solution require SuDS planning effort? |  |  | 117716.55
| Is an Environmental Impact Assessment (EIA) report required? |  |  | 24720.47
| Total Location Factor Costs |  |  | 160581.13
| On Cost |  |  | 415754.73
| Grand Total |  |  | 1753501.3241
Investment Code | I044106
Investment Title | AMP8 Sutton Staithe SWM
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Collection Storage - Offline | 03 - AW Water Recycling Infra | 1 | New | 355342.85 | Volume of Storage | 91 | m3
[5 empty] | Fencing | 48 | m
[5 empty] | Landscaping | 144 | m2
[5 empty] | Telemetry | 1 | Unit
[5 empty] | Road | 50 | m2
Sewer - Rising Main | 03 - AW Water Recycling Infra | 1 | New | 20869.05 | Length in Verge | 25 | m
[5 empty] | Length in Road type 3/4 | 25 | m
[5 empty] | Diameter | 150 | mm
Sewer - Gravity | 03 - AW Water Recycling Infra | 1 | New | 26297.85 | Length in Road Tpye 3/4 | 25 | m
[5 empty] | Length in Verge | 25 | m
[5 empty] | Depth | 2 | m
[5 empty] | Diameter | 150 | mm
| Total Asset direct costs |  |  | 402509.75
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 3842.11
| Does the solution need modelling prior to delivery? |  |  | 2886.98
| Total Location Factor Costs |  |  | 6729.09
| On Cost |  |  | 197838.26
| Grand Total |  |  | 607077.1
Investment Code | I044066
Investment Title | AMP8 Potter Heigham SWM Resilience
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Sewer Laterals | NFERSC | 100 | New | 522517.5781 | Quantity | 1 | Number
Sewer - Manhole | 03 - AW Water Recycling Infra | 50 | Refurbishment | 218514.8438 | Depth | 1.5 | m
[5 empty] | Diameter | 150 | mm
Sustainable drainage systems (SuDs) <#4> | STALSC | 1 | New | 87961.704 | Volume of downpipe disconnection | 4 | m3
[5 empty] | Number of properties disconnected | 100 | Number
Sustainable drainage systems (SuDs) | STALSC | 2 | New | 57115.8 | Volume of Pond | 100 | m3
[5 empty] | Volume of Wetland | 100 | m3
Sewer - Gravity | STALSC | 1 | New | 509570.382 | Length in Grassland | 1500 | m
[5 empty] | Depth | 1 | m
[5 empty] | Diameter | 100 | mm
| Total Asset direct costs |  |  | 1395680.3079
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 11501.7
| Does the solution need modelling prior to delivery? |  |  | 10010.46
| Does the solution require SuDS planning effort? |  |  | 139568.03
| Total Location Factor Costs |  |  | 161080.19
| On Cost |  |  | 457218.58
| Grand Total |  |  | 2013979.0779
Investment Code | I044069
Investment Title | AMP8 Horning SWM
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Sewer Laterals | NFERSC | 100 | New | 522517.5781 | Quantity | 1 | Number
Sewer - Manhole | 03 - AW Water Recycling Infra | 100 | New | 22684.82 | Depth | 1.5 | m
[5 empty] | Diameter | 150 | mm
CCTV Infra | 03 - AW Water Recycling Infra | 1 | New | 730029 | Diameter | 150 | mm
[5 empty] | Length | 5000 | m
| Total Asset direct costs |  |  | 1275231.3981
| On Cost |  |  | 323653.73
| Grand Total |  |  | 1598885.1281
Investment Code | I044108
Investment Title | AMP8 Tidal Outfall Protection
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Flap Valve | BLK - Balancing Lakes | 4 | New | 8593.095 | Nominal Bore | 225 | mm
Flap Valve <#2> | BLK - Balancing Lakes | 3 | New | 8964.4518 | Nominal Bore | 300 | mm
Flap Valve <#3> | BLK - Balancing Lakes | 1 | New | 6067.6991 | Nominal Bore | 575 | mm
Flap Valve <#4> | BLK - Balancing Lakes | 1 | New | 3828.0275 | Nominal Bore | 375 | mm
Flap Valve <#5> | BLK - Balancing Lakes | 1 | New | 10547.0423 | Nominal Bore | 975 | mm
Flap Valve <#6> | BLK - Balancing Lakes | 1 | New | 6347.658 | Nominal Bore | 600 | mm
Flap Valve <#7> | BLK - Balancing Lakes | 1 | New | 8027.4117 | Nominal Bore | 750 | mm
Flap Valve <#8> | BLK - Balancing Lakes | 1 | New | 1308.3969 | Nominal Bore | 150 | mm
Flap Valve <#9> | BLK - Balancing Lakes | 1 | New | 13906.5497 | Nominal Bore | 1275 | mm
| Total Asset direct costs |  |  | 67590.3318
| On Cost |  |  | 17769.5
| Grand Total |  |  | 85359.8318
Investment Code | I044093
Investment Title | AMP8 North Pickenham SWM
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Collection Storage - Offline | 03 - AW Water Recycling Infra | 1 | New | 364071.89 | Volume of Storage | 100 | m3
[5 empty] | Fencing | 48 | m
[5 empty] | Landscaping | 144 | m2
[5 empty] | Telemetry | 1 | Unit
[5 empty] | Road | 50 | m2
Sewer - Rising Main | 03 - AW Water Recycling Infra | 1 | New | 20869.05 | Length in Verge | 25 | m
[5 empty] | Length in Road type 3/4 | 25 | m
[5 empty] | Diameter | 150 | mm
Sewer - Gravity | 03 - AW Water Recycling Infra | 1 | New | 26297.85 | Length in Road Tpye 3/4 | 25 | m
[5 empty] | Length in Verge | 25 | m
[5 empty] | Depth | 2 | m
[5 empty] | Diameter | 150 | mm
| Total Asset direct costs |  |  | 411238.79
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 3897.9
| Does the solution need modelling prior to delivery? |  |  | 2949.59
| Total Location Factor Costs |  |  | 6847.49
| On Cost |  |  | 106110.3
| Grand Total |  |  | 524196.58
Investment ID | I043996
Investment Title | St Ives Somersham Rd River Inundation Prevention Resilience
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of measurement
Sewer - Manhole | SIVESC | 62 | Refurb | 270958.41 | Depth | 1.5 | m
[5 empty] | Diameter | 150 | mm
| Total Asset Costs |  |  | 270958.41
Group Adjustments
Site Wide Electrical Distribution
Total Location Factors
| On Cost |  |  | 68769.24
| Subtotal |  |  | 339727.65
Investment ID | I043571
Investment Title | Grimston Lateral Sealing from Groundwater
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of measurement
CCTV Infra <#2> | GRIMSC | 1 | Jetted | 15905.1007 | Length (m) | 3120 | m
Sewer - Gravity | GRIMSC | 1 | Refurbishment (reline) | 295495.5089 | Length in Grassland (m) | 1560 | m
[5 empty] | Depth (m) | 1 | m
[5 empty] | Diameter (nominal bore) (mm) | 100 | mm
| Total Asset Costs |  |  | 311400.6096
Group Adjustments
Site Wide Electrical Distribution
Total Location Factors
| On Cost |  |  | 79033.47
| Subtotal |  |  | 390434.0796
Investment ID | I043994
Investment Title | Burnham Market River Inundation Prevention Resilience
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of measurement
Sewer - Manhole | BUMKSC | 10 | Refurb | 43702.97 | Depth | 1 | m
[5 empty] | Diameter | 150 | mm
| Total Asset Costs |  |  | 43702.97
Group Adjustments
Site Wide Electrical Distribution
Total Location Factors
| On Cost |  |  | 11091.81
| Subtotal |  |  | 54794.78
Investment ID | I044000
Investment Title | Roydon Lateral Sealing from Groundwater resilience
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of measurement
CCTV Infra <#2> | GRIMSC | 1 | Jetted | 28772.8356 | Length (m) | 15860 | m
Sewer - Gravity | GRIMSC | 1 | Refurbishment (reline) | 1502102.1701 | Length in Grassland (m) | 7930 | m
[5 empty] | Depth (m) | 1 | m
[5 empty] | Diameter (nominal bore) (mm) | 100 | mm
| Total Asset Costs |  |  | 1530875.0057
Loading
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 31801.39
| On Cost |  |  | 396607.27
| Subtotal |  |  | 1959283.6657
Investment Code | I038882
Investment Title | AMP8 Pluvial and Fluvial Flood Resilience
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measurement
Flood gates | AW_WR_NI-SS-SBS | 10 | New | 259267.5232 | Gate Height | 1.5 | m
[5 empty] | Gate Width | 3 | m
Flood Wall (including coastal defence) <#4> | SBS - Site Services | 11 | New | 931203.39 | Wall Length | 50 | m
[5 empty] | Wall Height | 1 | m
Flood Embankment (Earth) | SBS - Site Services | 15 | New | 1409764.1744 | Embankment Volume | 600 | m3
De-mountable Barriers | AW_WR_NI-SS-BLD | 2 | New | 25419.8765 | Building Area (including perimeter) | 500 | m2
[5 empty] | Barrier Width | 5000 | mm
Water Resistant Doors | AW_WR_NI-SS-BLD | 11 | New | 75784.1509 | Door Size | Single
| Total Asset direct costs |  |  | 2701439.11
| On Cost |  |  | 710208.34
| Grand Total |  |  | 3411647.46

## SEMD
the cost show are total costs including Labour, Plant, materials and prelims, Location factors and On costs
Investment ID | I040803
Investment Title | SEMD water recycling risk evaluation
Specialist SEMD Engineering Resource | 2 FTE civil engineers over 5 years to undertake site inspections, risk assessments and programme development |  |  | 889850
On Cost |  |  |  | 217479.34
Grand Total |  |  |  | 1107329.34
Investment ID | I040591
Investment Title | Whitlingham STC SEMD
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 330792.896 | Length | 415 | m
Site Security CCTV | SS - Site Services | 1 | New | 59661.7034 | Number of Camera | 5 | Unit
Kiosks | SS - Site Services | 2 | New | 70859.7984 | Area | 20 | m2
Site Security CCTV <#2> | SS - Site Services | 1 | New | 25901.9806 | Number of Camera | 2 | Unit
Security Alarm | SBS - Site Services | 3 | New | 25753.2832 | Alarm Location | Door
[5 empty] | Area | 2 | m2
Gate (Mech) | SBS - Site Services | 2 | New | 9759.7768 | Width | 1.5 | m
[5 empty] | Height | 3000 | mm
Anti Climbing | SBS - Site Services | 1 | New | 607.29 | Length | 150 | m
Cabling Tray | CHP - CHP Plant | 1 | Refurbishment | 41027.9607 | Length | 200 | m
Cabling Ducting | CHP - CHP Plant | 1 | New | 88922.1413 | Length | 200 | m
Gate (Mech) <#2> | SBS - Site Services | 1 | New | 7753.4934 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 1 | New | 19091.4385 | Alarm Location | Building
[5 empty] | Area | 200 | m2
Security Locks | SBS - Site Services | 4 | New | 1076.3999 | Quantity | 1 | Unit
Security Locks <#2> | SBS - Site Services | 3 | New | 526.5193 | Quantity | 1 | Unit
External Site Lighting | SBS - Site Services | 7 | New | 23091.6902 | Quantity | 1 | Number
Telemetry Outstation | TEL - Telemetry | 2 | Refurbishment | 15700.5533 | Type | MM3X
Total Asset direct costs |  |  |  | 720526.9251
Wheel Clamps Adjustment. Quantity 4 |  |  |  | 1280.97
On Cost |  |  |  | 176409.85
Grand Total |  |  |  | 898217.7451
Investment ID | I040590
Investment Title | Pyewipe STC SEMD
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 375763.6027 | Length | 475 | m
Site Security CCTV | SS - Site Services | 1 | New | 59661.7034 | Number of Camera | 5 | Unit
Kiosks | SS - Site Services | 2 | New | 70859.7984 | Area | 20 | m2
Site Security CCTV <#2> | SS - Site Services | 1 | New | 25901.9806 | Number of Camera | 2 | Unit
Security Alarm | SBS - Site Services | 3 | New | 25753.2832 | Alarm Location | Door
[5 empty] | Area | 2 | m2
Gate (Mech) | SBS - Site Services | 2 | New | 9759.7768 | Width | 1.5 | m
[5 empty] | Height | 3000 | mm
Anti Climbing | SBS - Site Services | 1 | New | 607.29 | Length | 150 | m
Cabling Tray | CHP - CHP Plant | 1 | Refurbishment | 50855.7765 | Length | 250 | m
Cabling Ducting | CHP - CHP Plant | 1 | New | 108242.2814 | Length | 250 | m
Gate (Mech) <#2> | SBS - Site Services | 1 | New | 7753.4934 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 1 | New | 19091.4385 | Alarm Location | Building
[5 empty] | Area | 200 | m2
Security Locks | SBS - Site Services | 5 | New | 1345.4999 | Quantity | 1 | Unit
Security Locks <#2> | SBS - Site Services | 3 | New | 526.5193 | Quantity | 1 | Unit
External Site Lighting | SBS - Site Services | 7 | New | 23091.6902 | Quantity | 1 | Number
Telemetry Outstation | TEL - Telemetry | 2 | Refurbishment | 15700.5533 | Type | MM3X
Total Asset direct costs |  |  |  | 794914.6877
Wheel Clamps Adjustment. Quantity 4 |  |  |  | 1281.14
On Cost |  |  |  | 194590.26
Grand Total |  |  |  | 990786.0877
Investment ID | I040589
Investment Title | Kings Lynn STC SEMD
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 525665.9585 | Length | 675 | m
Site Security CCTV | SS - Site Services | 1 | New | 82168.1852 | Number of Camera | 7 | Unit
Kiosks | SS - Site Services | 2 | New | 141719.5968 | Area | 20 | m2
Site Security CCTV <#2> | SS - Site Services | 1 | New | 37155.2215 | Number of Camera | 3 | Unit
Security Alarm | SBS - Site Services | 5 | New | 42922.1387 | Alarm Location | Door
[5 empty] | Area | 2 | m2
Gate (Mech) | SBS - Site Services | 3 | New | 14639.6652 | Width | 1.5 | m
[5 empty] | Height | 3000 | mm
Anti Climbing | SBS - Site Services | 1 | New | 607.29 | Length | 200 | m
Cabling Tray | CHP - CHP Plant | 1 | Refurbishment | 70511.4081 | Length | 350 | m
Cabling Ducting | CHP - CHP Plant | 1 | New | 145596.1077 | Length | 350 | m
Gate (Mech) <#2> | SBS - Site Services | 2 | New | 15506.9869 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 2 | New | 38182.877 | Alarm Location | Building
[5 empty] | Area | 200 | m2
Security Locks | SBS - Site Services | 7 | New | 1883.6998 | Quantity | 1 | Unit
Security Locks <#2> | SBS - Site Services | 5 | New | 877.5321 | Quantity | 1 | Unit
External Site Lighting | SBS - Site Services | 10 | New | 32988.1288 | Quantity | 1 | Number
Telemetry Outstation | TEL - Telemetry | 2 | Refurbishment | 15700.5533 | Type | MM3X
Total Asset direct costs |  |  |  | 1166125.3498
Wheel Clamps Adjustment. Quantity 5 |  |  |  | 1601.43
On Cost |  |  |  | 285392.42
Grand Total |  |  |  | 1453119.1998
Investment ID | I040588
Investment Title | Great Billing STC SEMD
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 357025.8083 | Length | 450 | m
Site Security CCTV | SS - Site Services | 1 | New | 70914.9443 | Number of Camera | 6 | Unit
Kiosks | SS - Site Services | 2 | New | 141719.5968 | Area | 20 | m2
Site Security CCTV <#2> | SS - Site Services | 1 | New | 37155.2215 | Number of Camera | 3 | Unit
Security Alarm | SBS - Site Services | 5 | New | 42922.1387 | Alarm Location | Door
[5 empty] | Area | 2 | m2
Gate (Mech) | SBS - Site Services | 3 | New | 14639.6652 | Width | 1.5 | m
[5 empty] | Height | 3000 | mm
Anti Climbing | SBS - Site Services | 1 | New | 607.29 | Length | 200 | m
Cabling Tray | CHP - CHP Plant | 1 | Refurbishment | 65597.5002 | Length | 325 | m
Cabling Ducting | CHP - CHP Plant | 1 | New | 136392.9645 | Length | 325 | m
Gate (Mech) <#2> | SBS - Site Services | 2 | New | 15506.9869 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 2 | New | 38182.877 | Alarm Location | Building
[5 empty] | Area | 200 | m2
Security Locks | SBS - Site Services | 6 | New | 1614.5999 | Quantity | 1 | Unit
Security Locks <#2> | SBS - Site Services | 5 | New | 877.5321 | Quantity | 1 | Unit
External Site Lighting | SBS - Site Services | 9 | New | 29689.3159 | Quantity | 1 | Number
Telemetry Outstation | TEL - Telemetry | 2 | Refurbishment | 15700.5533 | Type | MM3X
Boundary Fencing <#2> | SBS - Site Services | 1 | New | 169647.8635 | Length | 200 | m
Total Asset direct costs |  |  |  | 1138194.8582
Wheel Clamps Adjustment. Quantity 5 |  |  |  | 1601.43
On Cost |  |  |  | 278566.21
Grand Total |  |  |  | 1418362.4982
Investment ID | I040587
Investment Title | Cotton Valley STC SEMD
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 394501.3972 | Length | 500 | m
Site Security CCTV | SS - Site Services | 1 | New | 59661.7034 | Number of Camera | 5 | Unit
Kiosks | SS - Site Services | 1 | New | 70859.7984 | Area | 20 | m2
Site Security CCTV <#2> | SS - Site Services | 1 | New | 25901.9806 | Number of Camera | 2 | Unit
Security Alarm | SBS - Site Services | 3 | New | 25753.2832 | Alarm Location | Door
[5 empty] | Area | 2 | m2
Gate (Mech) | SBS - Site Services | 3 | New | 14639.6652 | Width | 1.5 | m
[5 empty] | Height | 3000 | mm
Anti Climbing | SBS - Site Services | 1 | New | 607.29 | Length | 150 | m
Cabling Tray | CHP - CHP Plant | 1 | Refurbishment | 50855.7765 | Length | 250 | m
Cabling Ducting | CHP - CHP Plant | 1 | New | 108242.2814 | Length | 250 | m
Gate (Mech) <#2> | SBS - Site Services | 2 | New | 15506.9869 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 1 | New | 19091.4385 | Alarm Location | Building
[5 empty] | Area | 200 | m2
Security Locks | SBS - Site Services | 5 | New | 1345.4999 | Quantity | 1 | Unit
Security Locks <#2> | SBS - Site Services | 3 | New | 526.5193 | Quantity | 1 | Unit
External Site Lighting | SBS - Site Services | 7 | New | 23091.6902 | Quantity | 1 | Number
Telemetry Outstation | TEL - Telemetry | 1 | Refurbishment | 7850.2767 | Type | MM3X
Total Asset direct costs |  |  |  | 818435.5873
Wheel Clamps Adjustment. Quantity 4 |  |  |  | 1281.14
On Cost |  |  |  | 200338.77
Grand Total |  |  |  | 1020055.4973
Investment ID | I040584
Investment Title | Cambridge STC SEMD
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 375763.6027 | Length | 475 | m
Site Security CCTV | SS - Site Services | 1 | New | 59661.7034 | Number of Camera | 5 | Unit
Kiosks | SS - Site Services | 1 | New | 70859.7984 | Area | 20 | m2
Site Security CCTV <#2> | SS - Site Services | 1 | New | 25901.9806 | Number of Camera | 2 | Unit
Security Alarm | SBS - Site Services | 3 | New | 25753.2832 | Alarm Location | Door
[5 empty] | Area | 2 | m2
Gate (Mech) | SBS - Site Services | 2 | New | 9759.7768 | Width | 1.5 | m
[5 empty] | Height | 3000 | mm
Anti Climbing | SBS - Site Services | 1 | New | 607.29 | Length | 150 | m
Cabling Tray | CHP - CHP Plant | 1 | Refurbishment | 50855.7765 | Length | 250 | m
Cabling Ducting | CHP - CHP Plant | 1 | New | 108242.2814 | Length | 250 | m
Gate (Mech) <#2> | SBS - Site Services | 1 | New | 7753.4934 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 1 | New | 19091.4385 | Alarm Location | Building
[5 empty] | Area | 200 | m2
Security Locks | SBS - Site Services | 5 | New | 1345.4999 | Quantity | 1 | Unit
Security Locks <#2> | SBS - Site Services | 3 | New | 526.5193 | Quantity | 1 | Unit
External Site Lighting | SBS - Site Services | 7 | New | 23091.6902 | Quantity | 1 | Number
Telemetry Outstation | TEL - Telemetry | 1 | Refurbishment | 7850.2767 | Type | MM3X
Total Asset direct costs |  |  |  | 787064.411
Wheel Clamps Adjustment. Quantity 4 |  |  |  | 1281.14
On Cost |  |  |  | 192671.65
Grand Total |  |  |  | 981017.201
Investment ID | I040582
Investment Title | Chelmsford STC SEMD
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 357025.8083 | Length | 450 | m
Site Security CCTV | SS - Site Services | 1 | New | 59661.7034 | Number of Camera | 5 | Unit
Kiosks | SS - Site Services | 1 | New | 70859.7984 | Area | 20 | m2
Site Security CCTV <#2> | SS - Site Services | 1 | New | 25901.9806 | Number of Camera | 2 | Unit
Security Alarm | SBS - Site Services | 3 | New | 25753.2832 | Alarm Location | Door
[5 empty] | Area | 2 | m2
Gate (Mech) | SBS - Site Services | 2 | New | 9759.7768 | Width | 1.5 | m
[5 empty] | Height | 3000 | mm
Anti Climbing | SBS - Site Services | 1 | New | 607.29 | Length | 150 | m
Cabling Tray | CHP - CHP Plant | 1 | Refurbishment | 45941.8686 | Length | 225 | m
Cabling Ducting | CHP - CHP Plant | 1 | New | 98646.1625 | Length | 225 | m
Gate (Mech) <#2> | SBS - Site Services | 1 | New | 7753.4934 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 1 | New | 19091.4385 | Alarm Location | Building
[5 empty] | Area | 200 | m2
Security Locks | SBS - Site Services | 5 | New | 1345.4999 | Quantity | 1 | Unit
Security Locks <#2> | SBS - Site Services | 3 | New | 526.5193 | Quantity | 1 | Unit
External Site Lighting | SBS - Site Services | 7 | New | 23091.6902 | Quantity | 1 | Number
Telemetry Outstation | TEL - Telemetry | 1 | Refurbishment | 7850.2767 | Type | MM3X
Total Asset direct costs |  |  |  | 753816.5898
Wheel Clamps Adjustment. Quantity 4 |  |  |  | 1281.14
On Cost |  |  |  | 184545.89
Grand Total |  |  |  | 939643.6198
Investment ID | I040580
Investment Title | Basildon STC SEMD
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 469452.5751 | Length | 600 | m
Site Security CCTV | SS - Site Services | 1 | New | 70914.9443 | Number of Camera | 6 | Unit
Kiosks | SS - Site Services | 2 | New | 141719.5968 | Area | 20 | m2
Site Security CCTV <#2> | SS - Site Services | 1 | New | 25901.9806 | Number of Camera | 2 | Unit
Security Alarm | SBS - Site Services | 4 | New | 34337.7109 | Alarm Location | Door
[5 empty] | Area | 2 | m2
Gate (Mech) | SBS - Site Services | 3 | New | 14639.6652 | Width | 1.5 | m
[5 empty] | Height | 3000 | mm
Anti Climbing | SBS - Site Services | 1 | New | 607.29 | Length | 175 | m
Cabling Tray | CHP - CHP Plant | 1 | Refurbishment | 60683.5923 | Length | 300 | m
Cabling Ducting | CHP - CHP Plant | 1 | New | 127105.1701 | Length | 300 | m
Gate (Mech) <#2> | SBS - Site Services | 2 | New | 15506.9869 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 2 | New | 38182.877 | Alarm Location | Building
[5 empty] | Area | 200 | m2
Security Locks | SBS - Site Services | 6 | New | 1614.5999 | Quantity | 1 | Unit
Security Locks <#2> | SBS - Site Services | 4 | New | 702.0257 | Quantity | 1 | Unit
External Site Lighting | SBS - Site Services | 8 | New | 26390.503 | Quantity | 1 | Number
Telemetry Outstation | TEL - Telemetry | 2 | Refurbishment | 15700.5533 | Type | MM3X
Total Asset direct costs |  |  |  | 1043460.0713
Wheel Clamps Adjustment. Quantity 4 |  |  |  | 1281.14
On Cost |  |  |  | 255334.75
Grand Total |  |  |  | 1300075.9613
Investment ID | I040578
Investment Title | Ipswich Cliff Quay STC SEMD
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 225861.2469 | Length | 275 | m
Site Security CCTV | SS - Site Services | 1 | New | 82168.1852 | Number of Camera | 7 | Unit
Kiosks | SS - Site Services | 2 | New | 141719.5968 | Area | 20 | m2
Site Security CCTV <#2> | SS - Site Services | 1 | New | 37155.2215 | Number of Camera | 3 | Unit
Security Alarm | SBS - Site Services | 5 | New | 42922.1387 | Alarm Location | Door
[5 empty] | Area | 2 | m2
Gate (Mech) | SBS - Site Services | 3 | New | 14639.6652 | Width | 1.5 | m
[5 empty] | Height | 3000 | mm
Anti Climbing | SBS - Site Services | 1 | New | 607.29 | Length | 250 | m
Cabling Tray | CHP - CHP Plant | 1 | Refurbishment | 70511.4081 | Length | 350 | m
Cabling Ducting | CHP - CHP Plant | 1 | New | 145596.1077 | Length | 350 | m
Gate (Mech) <#2> | SBS - Site Services | 2 | New | 15506.9869 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 2 | New | 38182.877 | Alarm Location | Building
[5 empty] | Area | 200 | m2
Security Locks | SBS - Site Services | 7 | New | 1883.6998 | Quantity | 1 | Unit
Security Locks <#2> | SBS - Site Services | 5 | New | 877.5321 | Quantity | 1 | Unit
External Site Lighting | SBS - Site Services | 10 | New | 32988.1288 | Quantity | 1 | Number
Telemetry Outstation | TEL - Telemetry | 2 | Refurbishment | 15700.5533 | Type | MM3X
Boundary Fencing <#2> | SBS - Site Services | 1 | New | 319550.2193 | Length | 400 | m
Total Asset direct costs |  |  |  | 1185870.8575
Wheel Clamps Adjustment. Quantity 5 |  |  |  | 1601.43
On Cost |  |  |  | 290218.23
Grand Total |  |  |  | 1477690.5175
Investment ID | I040443
Investment Title | Colchester STC SEMD
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 544403.753 | Length | 700 | m
Site Security CCTV | SS - Site Services | 1 | New | 82168.1852 | Number of Camera | 7 | Unit
Kiosks | SS - Site Services | 2 | New | 141719.5968 | Area | 20 | m2
Site Security CCTV <#2> | SS - Site Services | 1 | New | 37155.2215 | Number of Camera | 3 | Unit
Security Alarm | SBS - Site Services | 5 | New | 42922.1387 | Alarm Location | Door
[5 empty] | Area | 2 | m2
Gate (Mech) | SBS - Site Services | 3 | New | 14639.6652 | Width | 1.5 | m
[5 empty] | Height | 3000 | mm
Anti Climbing | SBS - Site Services | 1 | New | 607.29 | Length | 250 | m
Cabling Tray | CHP - CHP Plant | 1 | Refurbishment | 119650.4871 | Length | 600 | m
Cabling Ducting | CHP - CHP Plant | 1 | New | 145596.1077 | Length | 350 | m
Gate (Mech) <#2> | SBS - Site Services | 2 | New | 15506.9869 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 2 | New | 38182.877 | Alarm Location | Building
[5 empty] | Area | 200 | m2
Security Locks | SBS - Site Services | 7 | New | 1883.6998 | Quantity | 1 | Unit
Security Locks <#2> | SBS - Site Services | 5 | New | 877.5321 | Quantity | 1 | Unit
External Site Lighting | SBS - Site Services | 10 | New | 32988.1288 | Quantity | 1 | Number
Telemetry Outstation | TEL - Telemetry | 2 | Refurbishment | 15700.5533 | Type | MM3X
Total Asset direct costs |  |  |  | 1234002.2233
Wheel Clamps Adjustment. Quantity 5 |  |  |  | 1601.43
On Cost |  |  |  | 301981.53
Grand Total |  |  |  | 1537585.1833
Investment ID | I039997
Investment Title | Site 1 WTW SEMD Compliance
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 195880.7758 | Length | 235 | m
Boundary Fencing <#2> | SS - Site Services | 1 | New | 124677.1568 | Length | 140 | m
Boundary Fencing <#3> | SS - Site Services | 1 | New | 33236.7197 | Length | 18 | m
Boundary Fencing <#4> | SS - Site Services | 1 | New | 207123.4525 | Length | 250 | m
Door (Security) | SBS - Site Services | 8 | New | 55115.7461 | Door Size | Single
Door (Security) <#2> | SBS - Site Services | 6 | New | 49166.5059 | Height | Double
Gate (Mech) | SBS - Site Services | 3 | New | 23260.4803 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Gate (Mech) <#2> | SBS - Site Services | 1 | New | 3922.0201 | Width | 1 | m
[5 empty] | Height | 3000 | mm
Access Hatch | SBS - Site Services | 1 | New | 16446.0844 | Area | 4 | m2
Security Alarm | SBS - Site Services | 1 | New | 8690.5592 | Alarm Location | Hatch
[5 empty] | Area | 4 | m2
Site Security CCTV | SS - Site Services | 6 | New | 87892.4382 | Number of Camera | 1 | Unit
Site Security CCTV <#2> | SS - Site Services | 1 | New | 14648.7397 | Number of Camera | 1 | Unit
Security Alarm <#2> | SBS - Site Services | 21 | New | 181387.3623 | Alarm Location | Door
[5 empty] | Area | 3 | m2
Security Alarm <#3> | SBS - Site Services | 20 | New | 172749.8689 | Alarm Location | Door
[5 empty] | Area | 3 | m2
Security Alarm <#4> | SBS - Site Services | 20 | New | 172749.8689 | Alarm Location | Building
[5 empty] | Area | 3 | m2
Cabling Ducting | SBS - Site Services | 1 | New | 111288.4423 | Length | 258 | m
Security Alarm <#5> | SBS - Site Services | 6 | New | 51188.1721 | Alarm Location | Door
[5 empty] | Area | 1 | m2
Special Purpose Security Cage | BLD - BUILDING | 2 | New | 67626.8148 | Cage Volume | 20 | m3
Boundary Fencing <#6> | SS - Site Services | 1 | New | 20792.029 | Length | 102 | m
Fan | BLD - BUILDING | 2 | New | 10432.1725 | Power | 0.1 | kW
Security Locks | SBS - Site Services | 5 | New | 1345.4999 | Quantity | 1 | Number
Security Locks <#2> | SBS - Site Services | 15 | New | 4019.2897 | Quantity | 1 | Number
Cabling Ducting <#2> | SBS - Site Services | 1 | New | 69332.3963 | Length | 290 | m
Cabling Tray | BOR - Borehole Abstraction | 1 | New | 73383.794 | Length | 725 | m
Total Asset direct costs |  |  |  | 1756356.3894
Site Wide Electrical Distribution |  |  |  | 85189.68
On Cost |  |  |  | 491508.65
Grand Total |  |  |  | 2333054.7194
Investment ID | I039997
Investment Title | Site 2 WTW SEMD Compliance
Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
Boundary Fencing | SS - Site Services | 1 | New | 117182.039 | Length | 130 | m
Boundary Fencing <#2> | SS - Site Services | 1 | New | 53473.5378 | Length | 40 | m
Door (Security) | SBS - Site Services | 3 | New | 20668.4048 | Door Size | Single
Door (Security) <#2> | SBS - Site Services | 4 | New | 32777.6706 | Door Size | Double
Gate (Mech) | SBS - Site Services | 1 | New | 7753.4934 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Security Alarm <#2> | SBS - Site Services | 10 | New | 86374.9345 | Alarm Location | Door
[5 empty] | Area | 3 | m2
Security Alarm <#3> | SBS - Site Services | 12 | New | 103649.9213 | Alarm Location | Door
[5 empty] | Area | 3 | m2
Security Alarm <#4> | SBS - Site Services | 10 | New | 86374.9345 | Alarm Location | Building
[5 empty] | Area | 3 | m2
Security Alarm <#5> | SBS - Site Services | 2 | New | 17062.724 | Alarm Location | Door
[5 empty] | Area | 1 | m2
Security Locks <#2> | SBS - Site Services | 8 | New | 2143.6212 | Quantity | 1 | Number
Security Alarm | SBS - Site Services | 2 | New | 17062.724 | Alarm Location | Door
[5 empty] | Area | 1 | m2
Cabling Ducting | CON - Common Control | 1 | New | 16308.1083 | Length | 7 | m
Cabling Tray <#2> | SBS - Site Services | 1 | New | 26653.4507 | Length | 260 | m
Total Asset direct costs |  |  |  | 587485.564
Site Wide Electrical Distribution |  |  |  | 5089.82
On Cost |  |  |  | 158158.36
Grand Total |  |  |  | 750733.744
Reference section 10.8 - PR24 Enhancement Strategies Part 1: Resilience to the risk of drought and flood
The investment asset breakdown provides an information of the assets used, such as fencing, alarm systems and CCTV as well as the key attributes. These costs include the labour, plant, material and prelims. We have used both the models relevant to each asset and the on-site design data to construct the key cost assumptions and estimations. We used our historic outturn cost data from previous similar projects which reflect the actual costs of procuring, installing and commissioning the solutions. By using our historic data and group delivery approach, we ensure that our cost estimation is realistic and efficient. Therefore, we have developed our cost forecasts drawing from our outturn costs and experience delivering similar projects. These reflect our lessons learned from delivering these schemes in the past, as well as the actual costs incurred. Our proposed costs reflect our continuous improvement in delivery in this area, ensuring that we capture the benefits of economies of scale, standardisation and optimisation of design and delivery.

## RWD - Nitrate
Investment ID | I038901 |  |  |  |  | the cost show are total costs including Labour, Plant, materials and prelims, Location factors and On costs
Investment Title | Two Mile Bottom WS Nitrate Compliance
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
RO/IX Plant | 1E - Soluble Compounds / Hydrocarbon Removal | 1 | New | 2191982.4916 | Flow | 9.22 | ML/D
Gate (Mech)- | SBS - Site Services | 1 | New | 7753.4934 | Width | 3 | m
[5 empty] | Height | 3000 | mm
External Site Lighting | BLD - BUILDING | 4 | New | 9955.0883 | Units | 1 | number
Fire Alarm Cntrl Pan | BLD - BUILDING | 2 | New | 32607.8243 | Area | 250 | m2
Chlorine Dosing | 1F - Final Disinfections | 1 | New | 341844.929 | Flow | 9.22 | ML/D
Landscaping | SS - Site Services | 1 | New | 58801.4182 | Area | 1700 | m2
Telemetry | SS - Site Services | 1 | New | 27286.0852 | Units | 2 | number
Standby Generation | SS - Site Services | 1 | New | 75912.248 | Total Installed Power | 37.07 | kW
Hardstanding Area | SBS - Site Services | 1 | New | 66496.9925 | Area | 480 | m2
Rigid Pipework -site drains | NIT - Nitrate Removal | 1 | New | 23688.0411 | Length | 40 | m
[5 empty] | Diameter | 150 | mm
Roads | SS - Site Services | 1 | New | 73491.6735 | Area | 540 | m2
Boundary Fencing | SS - Site Services | 1 | New | 126925.6921 | Length | 143 | m
Round Tank (Flatfloor) | NIT - Nitrate Removal | 1 | New | 90902.6781 | Volume | 40 | m3
Fixed Fire Suppression Cylinder | SBS - Site Services | 3 | New | 43178.4442 | Number of cylinders | 2 | number
Bund <#2> | NIT - Nitrate Removal | 1 | New | 93131.1994 | Volume | 60 | m3
Water Main | 01 - AW Water Infra | 2 | New | 2121610.4093 | Nominal Bore | 400 | mm
[5 empty] | Length in Field | 600 | m
[5 empty] | Length in Grassland | 800 | m
[5 empty] | Length of Directional Drill | 130 | m
[5 empty] | Depth | 3000 | mm
Security Alarm | INT - Interstage Pumping | 1 | New | 21744.7241 | Area | 250 | m2
Disinfection - Contact Tanks | 1F - Final Disinfections | 1 | New | 894115.6102 | Flow | 9.22 | ML/D
Welfare | SBS - Site Services | 1 | New | 88140.7884 | Area | 10 | m2
Septic Tank /Cesspit | SBS - Site Services | 1 | New | 49493.3438 | Volume | 15 | m3
Kiosks | SS - Site Services | 1 | New | 91772.1806 | Security Level | LPBC4
[5 empty] | Area | 14 | m2
Process Building <#2> | SBS - Site Services | 1 | New | 462021.1023 | Area | 240 | m2
Lagoon | DWW - Dirty Wash Water Handling | 1 | New | 52518.1249 | Lagoon Use (Namecode) | Run to Waste Lagoon
[5 empty] | Capacity | 1175 | m3
Rigid Pipework <#2>- | NIT - Nitrate Removal | 1 | New | 23688.0411 | Length | 40 | m
[5 empty] | Diameter | 150 | mm
Kiosks <#2> | SS - Site Services | 1 | New | 151132.7098 | Security Level | LPBC4
[5 empty] | Area | 25 | m2
Kiosks <#3> | SS - Site Services | 1 | New | 48600.8866 | Security Level | LPBC4
[5 empty] | Area | 6 | m2
Rigid Pipework <#3> | CHL - Chlorination | 1 | New | 29610.0514 | Length | 50 | m
[5 empty] | Diameter | 150 | mm
Water Main <#2> | 01 - AW Water Infra | 1 | New | 105628.9509 | Nominal Bore | 75 | mm
[5 empty] | Length in Field | 65 | m
[5 empty] | Length in Grassland | 800 | m
[5 empty] | Length in Type 3/4 Reinstatement | 10 | m
[5 empty] | Depth | 900 | mm
Rigid Pipework <#5> | CHL - Chlorination | 2 | New | 111840.6913 | Length | 60 | m
[5 empty] | Diameter | 310 | mm
Flap Valve | CHL - Chlorination | 1 | New | 4107.9864 | Nominal Bore | 400 | mm
Bund <#3> | NIT - Nitrate Removal | 1 | New | 93131.1994 | Volume | 60 | m3
Fire Alarm Cntrl Pan <#2> | BLD - BUILDING | 2 | New | 27155.7507 | Area | 150 | m2
Kiosks <#4> | SS - Site Services | 1 | New | 161925.5333 | Security Level | LPBC4
[5 empty] | Area | 27 | m2
Biodiversity Net Gain | SS - Site Services | 1 | New | 15900 | Units | 0.53 | number
Interstage Pumping <#2> | 1G - Final Water Conditioning | 1 | New | 220391.27 | Total Installed Power (inc standby) | 3 | kW
Supply | 1H - Treated Water Pumping | 1 | New | 741904.2915 | Total Installed Power (inc standby) | 75 | kW
NRV unit - Valve only | SBS - Site Services | 1 | New | 2537.4302 | Nominal Bore | 150 | mm
Kiosk - Sampling Kiosk (incl pipework+chamber) | SBS - Site Services | 1 | New | 30962.8843 | Area | 25 | m2
Total Asset direct costs |  |  |  | 8813892.2595
| Site wide Electrical Distribution |  |  | 506798.8
Location Factors
| Are access amendments required at the site to enable the works to be carried out? |  |  | 95614.58
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 136154.25
| Do the works cross other significant infrastructure - rail lines, open water, major roads, medium and high pressure gas lines? |  |  | 242968.31
| Does the site have poor ground conditions - does it need piling? |  |  | 249794.52
| Does the solution need modelling prior to delivery? |  |  | 34676.93
| Does the solution require an extensive planning effort? |  |  | 1246906.42
| Does the statutory power supply need upgrading? |  |  | 125301.7
| Is an Environmental Impact Assessment (EIA) report required? |  |  | 195734.51
| Total Location Factor Costs ( access ammendments, Power upgarde , EIA, modelling , dewatering , land purchase) |  |  | 2327151.22
| On Cost |  |  | 4574101.02
| Grand Total |  |  | 16221943.2995
| Investment ID | I039572
| Investment Title | Marham WTW Nitrate Compliance
Activity Type | Name | Functional Location | Quantity | Asset Origin | Capital Cost (£) | Attribute | Value | Unit of Measure
New | Security Alarm | BLD - BUILDING | 1 | New | 21744.7241 | Area | 250 | m2
New | Gate (Mech) | SBS - Site Services | 1 | New | 7753.4934 | Width | 3 | m
[6 empty] | Height | 3000 | mm
New | External Site Lighting | BLD - BUILDING | 1 | New | 2488.7721 | Lighting Type | Lighting Fixed On Buildings
New | Fire Alarm Cntrl Pan | BLD - BUILDING | 1 | New | 13577.8753 | Building floor area protected | 150 | m2
New | Standby Generation | SS - Site Services | 1 | New | 57122.76 | Total Installed Power | 18.4 | kW
New | Hardstanding Area | SBS - Site Services | 1 | New | 23416.894 | Area | 100 | m2
New | Biodiversity Net Gain | SS - Site Services | 1 | New | 15900 | Units | 0.53 | Number
New | Landscaping | SS - Site Services | 1 | New | 48849.3252 | Area | 1300 | m2
New | Boundary Fencing | SS - Site Services | 1 | New | 177142.9813 | Length | 210 | m
New | Roads | SS - Site Services | 1 | New | 22954.121 | Area | 140 | m2
New | RO/IX Plant | 1E - Soluble Compounds / Hydrocarbon Removal | 1 | New | 2919608.4839 | Flow | 21.16 | Ml/d
New | Rigid Pipework <#2> | NIT - Nitrate Removal | 1 | New | 517245.05 | Length | 350 | m
[6 empty] | Diameter | 350 | mm
New | Fixed Fire Suppression Cylinder | SBS - Site Services | 1 | New | 14392.8147 | Number of Cylinders | 2 | Number
New | Fire Alarm Cntrl Pan <#2> | BLD - BUILDING | 1 | New | 16303.9122 | Building floor area protected | 250 | m2
New | Bund <#2> | SBS - Site Services | 1 | New | 275411.4025 | Volume | 180 | m3
New | Round Tank (Flatfloor) <#2> | NIT - Nitrate Removal | 1 | New | 215428.4374 | Volume | 160 | m3
New | Lagoon | SBS - Site Services | 1 | New | 20673.6363 | Capacity | 373 | m3
New | NRV unit | SBS - Site Services | 1 | New | 2537.4302 | Diameter | 350 | mm
New | Flap Valve | NIT - Nitrate Removal | 1 | New | 3548.0685 | Diameter | 350 | mm
New | Rigid Pipework <#3> | NIT - Nitrate Removal | 1 | New | 517245.05 | Length | 350 | m
[6 empty] | Diameter | 350 | mm
New | Process Building <#2> | SBS - Site Services | 1 | New | 474483.3204 | Area | 250 | m2
New | Fixed Fire Suppression Cylinder <#2> | SBS - Site Services | 1 | New | 14392.8147 | Number of Cylinders | 2 | Number
New | Interstage Pumping | 1G - Final Water Conditioning | 1 | New | 496752.74 | Total Installed Power | 80 | kW
New | Kiosks | SS - Site Services | 1 | New | 161925.5333 | Area | 27 | m2
New | Interstage Pumping <#2> | 1G - Final Water Conditioning | 1 | New | 220391.27 | Total Installed Power | 3 | kW
New | Rigid Pipework | NIT - Nitrate Removal | 2 | New | 1755757.92 | Length | 420 | m
[6 empty] | Diameter | 500 | mm
| Total Asset direct costs |  |  |  | 8017048.8306
| Site Wide Electrical Distibution |  |  |  | 460980.31
Location Factors
| Does the solution require an extensive planning effort? |  |  |  | 1134176.52
| Does the statutory power supply need upgrading? |  |  |  | 113973.46
| Is an Environmental Impact Assessment (EIA) report required? |  |  |  | 178038.61
| Total Location Factor Costs ( planning , statutory power upgrade, EIA report) |  |  |  | 1426188.59
| On Cost |  |  |  | 3917230.82
| Grand Total |  |  |  | 13821448.5506

## RWD - PFAS
the cost show are total costs including Labour, Plant, materials and prelims, Location factors and On costs
Investment ID | I039133
Investment Title | Parsonage St WTW WQ Compliance
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
G.A.C (Volume) | 1E - Soluble Compounds / Hydrocarbon Removal | 1 | New | 2618039.2297 | Total Volume | 200 | m3
Closed Rectangular Tank (Level Floor)- Clean Wash Water Tank | DWW - Dirty Wash Water Handling | 2 | New | 290904.6229 | Total Volume | 90 | m3
Disinfection - Chlorine Dosing, Sodium Hypochlorite | 1F - Final Disinfections | 1 | New | 79393.425 | Flow | 2.42 | ML/d
Kiosks - LPBC3 | SS - Site Services | 1 | New | 74263.4251 | Area | 21 | m2
UV Disinfection - Civil | 1F - Final Disinfections | 1 | New | 9283.85 | Flow | 2420 | m3/d
UV Disinfection - M&E | 1F - Final Disinfections | 1 | New | 457432.2161 | Flow | 2420 | m3/d
Kiosks <#2> LPBC3 | SS - Site Services | 1 | New | 138932.3326 | Area | 40 | m2
Boundary Fencing - High Security | SS - Site Services | 1 | New | 117182.039 | Length | 130 | m
Water Main | 01 - AW Water Infra | 1 | New | 481452.5 | Nominal Bore | 250 | mm
[5 empty] | Length in Type 3/4 Reinstatement (m) | 500 | m
[5 empty] | Depth | 2000 | mm
Rigid Pipework <#2> | GAC - GAC Adsorption | 1 | New | 30716.8 | Length | 40 | m
[5 empty] | Diameter | 200 | mm
Rigid Pipework <#3> | GAC - GAC Adsorption | 1 | New | 23179.25 | Length | 25 | m
[5 empty] | Diameter | 250 | mm
Butterfly Valve | GAC - GAC Adsorption | 5 | New | 7721.4453 | Nominal Bore | 250 | mm
Electrical Actuator <#2> | GAC - GAC Adsorption | 5 | New | 61255.8379 | Diameter | 250 | mm
Water Main <#3> | 01 - AW Water Infra | 1 | new | 223515.63 | Nominal Bore | 150 | mm
[5 empty] | Length in Field (m) | 1170 | m
[5 empty] | Depth | 2000 | mm
Chamber <#2> | DWW - Dirty Wash Water Handling | 1 | New | 17411.2847 | Total Volume | 5 | m3
Outfall Pipework- River | DWW - Dirty Wash Water Handling | 1 | New | 9963.1403 | Length | 2 | m
[5 empty] | Diameter | 150 | mm
Rigid Pipework <#7> | GAC - GAC Adsorption | 1 | New | 13394.25 | Length | 50 | m
[5 empty] | Diameter | 25 | mm
Interstage Pumping | 1G - Final Water Conditioning | 1 | New | 299351.69 | Total Installed Power (inc standby) | 25 | kW
Interstage Pumping <#2> | 1G - Final Water Conditioning | 1 | New | 274227.92 | Total Installed Power (inc standby) | 18 | kW
Interstage Pumping <#4> | 1G - Final Water Conditioning | 1 | New | 245515.04 | Total Installed Power (inc standby) | 10 | kW
Chamber <#3> | GAC - GAC Adsorption | 2 | New | 24679.801 | Total Volume | 3 | m3
Magflow | GAC - GAC Adsorption | 2 | New | 12746.8398 | Diameter | 250 | mm
Pressure Regulating Valve | GAC - GAC Adsorption | 1 | New | 12380.0455 | Nominal Bore | 250 | mm
Turbidity Monitor | GAC - GAC Adsorption | 2 | New | 15309.1465 | Units | 1 | number
Ammonia Monitor (ISE Chem) | GAC - GAC Adsorption | 1 | New | 24701.984 | Units | 1 | number
Roads | SS - Site Services | 1 | New | 114150.5401 | Area | 900 | m2
Landscaping | SS - Site Services | 1 | New | 58801.4182 | Area | 1700 | m2
Boundary Fencing <#2> General | SS - Site Services | 1 | New | 41388.3466 | Length | 220 | m
Transformer | GAC - GAC Adsorption | 1 | New | 25615.4354 | Capacity | 250 | kW
Kiosks <#3> LPBC3 | SS - Site Services | 1 | New | 53841.6648 | Area | 15 | m2
Standby Generation | SS - Site Services | 1 | New | 242683.9985 | Total Installed Power | 250 | kW
Buildings | SS - Site Services | 1 | New | 171086.5293 | Area | 60 | m2
Dirty Wash Water Handling Plant (Civil) | 1J - Water Sludge Treatment | 2 | New | 223144.2078 | Tank Volume | 150 | m3
Dirty Wash Water Handling | 1J - Water Sludge Treatment | 1 | New | 133244.819 | Total Installed Power (inc standby) | 3 | kW
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Units | 1 | number
| Total asset costs |  |  | 6640553.7477
| Site wide Electrical Distribution |  |  | 381831.8405 | for new treatment process
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 102581.1959 | 3600 sq meters
| Does the solution need modelling prior to delivery? |  |  | 26126.2598 | to confirm correct sizing of equipment
| Does the solution require an extensive planning effort? |  |  | 939442.9675 | new site
| Does the statutory power supply need upgrading? |  |  | 94404.6775 | for new treatment process
| Is an Environmental Impact Assessment (EIA) report required? |  |  | 147470.0974 | new site
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 180036.5049 | modification and removal at existing site
| Total Location factors ( lad purcahse, planning , power upgrade, EIA, enabling works) |  |  | 1490061.703
| On Cost |  |  | 3389277.3672
| Total project CAPEX cost |  |  | 11901724.6583
Investment ID | I039195
Investment Title | Ulceby WTW WQ Compliance
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
G.A.C (Volume) | 1E - Soluble Compounds / Hydrocarbon Removal | 1 | New | 4884696.3125 | Total Volume | 640 | m3
Closed Rectangular Tank (Level Floor) - Clean Wash Water Tank | DWW - Dirty Wash Water Handling | 2 | New | 374122.0889 | Total Volume | 150 | m3
Boundary Fencing - High Security | SS - Site Services | 1 | New | 132172.2746 | Length | 150 | m
Water Main | 01 - AW Water Infra | 1 | New | 180137.4651 | Nominal Bore | 400 | mm
[5 empty] | Length in Verge/Unmade | 100 | m
[5 empty] | Length of Directional Drill | 100 | m
[5 empty] | Depth | 3000 | mm
Water Main <#2> | 01 - AW Water Infra | 1 | New | 180137.4651 | Nominal Bore | 400 | mm
[5 empty] | Length in Verge/Unmade | 100 | m
[5 empty] | Length of Directional Drill | 100 | m
[5 empty] | Depth | 3000 | mm
Rigid Pipework | SBS - Site Services | 1 | New | 302924.3 | Length | 350 | m
[5 empty] | Diameter | 200 | mm
Rigid Pipework <#2> | SBS - Site Services | 1 | New | 63221.4 | Length | 45 | m
[5 empty] | Diameter | 400 | mm
Water Main <#3> | 01 - AW Water Infra | 1 | New | 185369.6664 | Nominal Bore | 400 | mm
[5 empty] | Length in Field | 450 | m
[5 empty] | Depth | 900 | mm
Rigid Pipework <#4> | SBS - Site Services | 1 | New | 80365.5 | Length | 300 | m
[5 empty] | Diameter | 25 | mm
Water Main <#4> | 01 - AW Water Infra | 1 | New | 114438.3401 | Nominal Bore | 400 | mm
[5 empty] | Length in Verge/Unmade | 130 | m
[5 empty] | Length of Directional Drill | 100 | m
[5 empty] | Depth | 3000 | mm
Chamber | SBS - Site Services | 1 | New | 12339.9005 | Total Volume | 3 | m3
Chamber <#2> | SBS - Site Services | 1 | New | 17411.2847 | Total Volume | 5 | m3
Chambers/Cover & frame | 01 - AW Water Infra | 4 | New | 5056.52 | Surface Type (Infra) | Unmade
[5 empty] | Chamber Size (Infra) | up to 600 x 900mm
Rigid Pipework <#5> | SBS - Site Services | 1 | New | 49172.2 | Length | 35 | m
[5 empty] | Diameter | 400 | mm
Interstage Pumping | 1G - Final Water Conditioning | 1 | New | 281406.14 | Total Installed Power (inc standby) | 20 | kW
Interstage Pumping <#3> | 1G - Final Water Conditioning | 1 | New | 428559.65 | Total Installed Power (inc standby) | 61 | kW
Interstage Pumping <#4> | 1G - Final Water Conditioning | 1 | New | 324475.46 | Total Installed Power (inc standby) | 32 | kW
Magflow | SBS - Site Services | 2 | New | 17339.9172 | Diameter | 400 | mm
Electrical Actuator <#3> | SBS - Site Services | 8 | New | 130373.4426 | Diameter | 400 | mm
Butterfly Valve <#3> | SBS - Site Services | 8 | New | 22812.6088 | Nominal Bore | 400 | mm
Pressure Regulating Valve | GAC - GAC Adsorption | 1 | New | 19808.0728 | Nominal Bore | 400 | mm
Roads | SS - Site Services | 1 | New | 251485.761 | Area | 2250 | m2
Dirty Wash Water Handling Plant (Civil) | 1J - Water Sludge Treatment | 2 | New | 886202.2629 | Total Volume | 300 | m3
Dirty Wash Water Handling | 1J - Water Sludge Treatment | 1 | New | 168715.9771 | Total Installed Power (inc standby) | 5 | kW
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Units | 1 | number
| Total asset costs |  |  | 9126387.0527
| Site wide Electrical Distribution |  |  | 524767.2555
| Does the solution need modelling prior to delivery? |  |  | 4821.2147
| Does the solution require an extensive planning effort? |  |  | 13850.9196
| Does the solution require environmental mitigation measures to be implemented? |  |  | 18895.5286
| Is an Environmental Impact Assessment (EIA) report required? |  |  | 202674.2405
| Total Location Factors ( Extensive planning , enviromental mitigations, modelling, EIA) |  |  | 240241.9034
| On Cost |  |  | 3912382.746
| Total project CAPEX cost |  |  | 13803778.9576
Investment ID | I039836
Investment Title | Beck Row WTW WQ Compliance
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Water Main | 01 - AW Water Infra | 1 | New | 382797.5775 | Nominal Bore | 80 | mm
[5 empty] | Length in Verge/Unmade | 500 | m
[5 empty] | Length in Field | 2500 | m
[5 empty] | Depth | 900 | mm
Chamber | GAC - GAC Adsorption | 1 | New | 17411.2847 | Volume | 5 | m3
Chamber <#2> | GAC - GAC Adsorption | 1 | New | 17411.2847 | Volume | 5 | m3
Interstage Pumping <#4> | 1G - Final Water Conditioning | 1 | New | 245515.04 | Total Installed Power (inc standby) | 10 | kW
Magflow | GAC - GAC Adsorption | 1 | New | 3770.676 | Diameter | 80 | mm
Chamber <#3> | GAC - GAC Adsorption | 2 | New | 34822.5694 | Volume | 5 | m3
Dirty Wash Water Handling Plant (Civil) | 1J - Water Sludge Treatment | 2 | New | 203313.3089 | Tank Volume | 120 | m3
Landscaping | SS - Site Services | 1 | New | 15194.9496 | Area | 240 | m2
Water Main <#2> | 01 - AW Water Infra | 1 | New | 87612 | Nominal Bore | 400 | mm
[5 empty] | Length in Field | 100 | m
[5 empty] | Depth | 2000 | mm
Interstage Pumping | 1G - Final Water Conditioning | 1 | New | 317297.24 | Total Installed Power (inc standby) | 30 | kW
Outfall Pipework - River | SBS - Site Services | 1 | New | 12229.8463 | Diameter | 100 | mm
[5 empty] | Length | 5 | m
PLC | DWW - Dirty Wash Water Handling | 1 | Upgrade | 17846.1052 | In/Out Cards (number) | 4 | number
Kiosks- LPCB4 | SS - Site Services | 1 | New | 188907.592 | Area | 32 | m2
Telemetry Outstation | TEL - Telemetry | 1 | Upgrade | 7565.1207 | Type of Telemetry Outstation | MM4 | units
G.A.C (Volume) | 1E - Soluble Compounds / Hydrocarbon Removal | 1 | New | 946664.9178 | Total Volume | 30 | m3
Dirty Wash Water Handling | 1J - Water Sludge Treatment | 1 | New | 386103.1379 | Total Installed Power (inc standby) | 30 | kW
Rigid Pipework | GAC - GAC Adsorption | 1 | New | 56343.3 | Diameter | 80 | mm
[5 empty] | Length | 150 | m
Rigid Pipework <#2> | GAC - GAC Adsorption | 1 | New | 29770 | Diameter | 50 | mm
[5 empty] | Length | 100 | m
| Total asset costs |  |  | 2970575.9507
| Site wide Electrical Distribution |  |  | 170808.1172
| Does the solution need modelling prior to delivery? |  |  | 11687.2842
| Does the solution require an extensive planning effort? |  |  | 420249.0925
| Total Location Factors ( Extensive planning , modelling) |  |  | 431936.3768
| On Cost |  |  | 1478127.4037
| Total project CAPEX cost |  |  | 5051447.8483
Investment ID | I040312
Investment Title | Barrow WTW WQ Compliance - DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
G.A.C (Volume) | 1E - Soluble Compounds / Hydrocarbon Removal | 1 | New | 8504347.2196 | Total Volume | 1800 | m3
Closed Rectangular Tank (Level Floor) - Clean Wash Water Tank | DWW - Dirty Wash Water Handling | 2 | New | 456814.685 | Total Volume | 225 | m3
Boundary Fencing - High security | SS - Site Services | 1 | New | 244599.0414 | Length | 300 | m
Rigid Pipework | GAC - GAC Adsorption | 1 | New | 399746.88 | Length | 160 | m
[5 empty] | Diameter | 600 | mm
Rigid Pipework <#2> | GAC - GAC Adsorption | 1 | New | 71467.2 | Length | 35 | m
[5 empty] | Diameter | 600 | mm
Rigid Pipework <#4> | GAC - GAC Adsorption | 1 | New | 252293.7 | Length | 150 | m
[5 empty] | Diameter | 400 | mm
Electrical Actuator | GAC - GAC Adsorption | 15 | New | 296800.2558 | Diameter | 600 | mm
Butterfly Valve | GAC - GAC Adsorption | 15 | New | 72603.5547 | Diameter | 600 | mm
Rigid Pipework <#5> | GAC - GAC Adsorption | 1 | New | 91886.4 | Length | 45 | m
[5 empty] | Diameter | 600 | mm
Electrical Actuator <#2> | GAC - GAC Adsorption | 15 | New | 296800.2558 | Diameter | 600 | mm
Butterfly Valve <#2> | GAC - GAC Adsorption | 15 | New | 72603.5547 | Diameter | 600 | mm
Rigid Pipework <#6> | GAC - GAC Adsorption | 1 | New | 187381.35 | Length | 75 | m
[5 empty] | Diameter | 600 | mm
Chamber | GAC - GAC Adsorption | 1 | New | 17411.2847 | Total Volume | 5 | m3
Chamber <#2> | GAC - GAC Adsorption | 1 | New | 17411.2847 | Total Volume | 5 | m3
Chambers/Cover & frame | 01 - AW Water Infra | 3 | New | 3792.39 | Surface Type (Infra) | Unmade
[5 empty] | Chamber Size (Infra) | up to 600 x 900mm
Rigid Pipework <#7> | GAC - GAC Adsorption | 1 | New | 49603.725 | Length | 75 | m
[5 empty] | Diameter | 150 | mm
Electrical Actuator <#3> | GAC - GAC Adsorption | 2 | New | 15708.5666 | Diameter | 150 | mm
Butterfly Valve <#3> | GAC - GAC Adsorption | 2 | New | 1585.8713 | Diameter | 150 | mm
Rigid Pipework <#8> | GAC - GAC Adsorption | 1 | New | 19198 | Length | 25 | m
[5 empty] | Diameter | 200 | mm
Gate Valve | GAC - GAC Adsorption | 4 | New | 29243.1515 | Diameter | 600 | mm
Interstage Pumping | 1G - Final Water Conditioning | 1 | New | 1027941.02 | Total Installed Power (inc standby) | 228 | kW
Interstage Pumping <#3> | 1G - Final Water Conditioning | 1 | New | 324475.46 | Total Installed Power (inc standby) | 32 | kW
Interstage Pumping <#4> | 1G - Final Water Conditioning | 1 | New | 236183.354 | Total Installed Power (inc standby) | 7.4 | kW
Magflow | GAC - GAC Adsorption | 2 | New | 23464.0204 | Diameter | 600 | mm
Chamber <#3> | GAC - GAC Adsorption | 2 | New | 34822.5694 | Total Volume | 5 | m3
Butterfly Valve <#4> | GAC - GAC Adsorption | 1 | New | 4840.237 | Diameter | 600 | mm
Electrical Actuator <#4> | GAC - GAC Adsorption | 1 | New | 19786.6837 | Diameter | 600 | mm
Pressure Regulating Valve | GAC - GAC Adsorption | 1 | New | 29712.1092 | Diameter | 600 | mm
Cabling Ducting | GAC - GAC Adsorption | 1 | New | 58417.9295 | Length | 300 | m
Roads | SS - Site Services | 1 | New | 21533.5964 | Area | 130 | m2
Rigid Pipework <#3> | GAC - GAC Adsorption | 1 | New | 10715.4 | Length | 40 | m
[5 empty] | Diameter | 25 | mm
Dirty Wash Water Handling Plant (Civil) | 1J - Water Sludge Treatment | 2 | New | 2404693.1892 | Total Volume | 450 | m3
Rigid Pipework <#9> | GAC - GAC Adsorption | 1 | New | 274825.98 | Length | 110 | m
[5 empty] | Diameter | 600 | mm
Landscaping | SS - Site Services | 1 | New | 43522.2345 | Area | 1100 | m2
Biodiversity Net Gain | SS - Site Services | 1 | New | 16800 | Units | 0.56
Standby Generation | SS - Site Services | 1 | New | 80571.88 | Total Installed Power | 41.7 | kW
| Total asset costs |  |  | 15713604.0344
| Site wide Electrical Distribution |  |  | 903532.232
| Does the site have a high water table - does it need dewatering? |  |  | 574490.6198 | site has high water table
| Does the site have poor ground conditions - does it need piling? |  |  | 445339.2519 | site has poor ground due to proximity to river
| Does the solution need modelling prior to delivery? |  |  | 61822.8114 | to confirm correct sizing of equipment
| Does the solution require an extensive planning effort? |  |  | 2223012.623 | for new plant
| Does the statutory power supply need upgrading? |  |  | 223390.6654 | for new treatment process
| Total Location Factors ( piling, Extensive planning , enviromental mitigations, modelling, EIA) |  |  | 3528055.9716
| On Cost |  |  | 7722589.4011
| Total project CAPEX cost |  |  | 27867781.639
Investment ID | I043556
Investment Title | Southfields PFAS Compliance - DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
G.A.C (Volume) | 1E - Soluble Compounds / Hydrocarbon Removal | 1 | New | 2618039.2297 | Total Volume | 200 | m3
Sludge Holding Tank | 1J - Water Sludge Treatment | 1 | New | 389636.9903 | Total Volume | 300 | m3
Dirty Wash Water Handling | 1J - Water Sludge Treatment | 1 | New | 122479.7804 | Total Installed Power (inc standby) | 2.5 | kW
Dirty Wash Water Handling Plant (Civil) | 1J - Water Sludge Treatment | 1 | New | 443101.1314 | Total Volume | 300 | m3
Chamber | DWW - Dirty Wash Water Handling | 1 | New | 17411.2847 | Total Volume | 5 | m3
Pressure Regulating Valve | BOR - Borehole Abstraction | 1 | New | 14856.0546 | Nominal Bore | 300 | mm
Cabling Ducting | GAC - GAC Adsorption | 1 | New | 163774.4831 | Length | 400 | m
Chlorine Dosing | 1F - Final Disinfections | 1 | New | 292685.315 | Flow | 5.5 | ML/D
Kiosks - LPBC4 | SS - Site Services | 1 | New | 151132.7098 | Area | 25 | m2
Lance Injector - Phosphate Injector | PHO - Phosphate Dosing | 4 | New | 3971.8387 | Flow | 5.5 | ML/D
Rigid Pipework <#8> dosing line | PHO - Phosphate Dosing | 4 | New | 59779.52 | Length | 100 | m
[5 empty] | Diameter | 25 | mm
Roads | SS - Site Services | 1 | New | 97548.7075 | Area | 750 | m2
Boundary Fencing -High Security | SS - Site Services | 1 | New | 394501.3972 | Length | 500 | m
Landscaping | SS - Site Services | 1 | New | 42145.0432 | Area | 1050 | m2
Supply | 1H - Treated Water Pumping | 1 | New | 802320.8087 | Total Installed Power (inc standby) | 96 | kW
Supply <#2> | 1H - Treated Water Pumping | 1 | New | 632579.1652 | Total Installed Power (inc standby) | 37 | kW
Gate (Mech) | GAC - GAC Adsorption | 1 | New | 7753.4934 | Width | 3 | m
[5 empty] | Height | 3000 | mm
Disinfection - Contact Tanks | 1F - Final Disinfections | 1 | New | 783020.005 | Flow | 5.5 | ML/D
Water Main | 01 - AW Water Infra | 1 | New | 13564.4724 | Nominal Bore | 300 | mm
[5 empty] | Length in Verge/Unmade | 35 | m
[5 empty] | Depth | 900 | mm
Water Main <#2> | 01 - AW Water Infra | 1 | New | 14259.9782 | Nominal Bore | 300 | mm
[5 empty] | Length in Field | 45 | m
[5 empty] | Depth | 900 | mm
Water Main <#3> | 01 - AW Water Infra | 1 | New | 6478.7696 | Nominal Bore | 150 | mm
[5 empty] | Length in Field | 35 | m
[5 empty] | Depth | 900 | mm
Water Main <#5> | 01 - AW Water Infra | 1 | New | 15844.4202 | Nominal Bore | 300 | mm
[5 empty] | Length in Field | 50 | m
[5 empty] | Depth | 900 | mm
Water Main <#6> | 01 - AW Water Infra | 1 | New | 8752.8514 | Nominal Bore | 50 | mm
[5 empty] | Length in Field | 90 | m
[5 empty] | Depth | 900 | mm
Biodiversity Net Gain | 01 - AW Water Infra | 1 | New | 16800 | Units | 0.56 | number
Closed Rectangular Tank (Sloped Floor) | FIN - Final Water Pumping | 2 | New | 642688.22 | Total Volume | 450 | m3
Static Mixer | PHO - Phosphate Dosing | 2 | New | 28711.6482 | Nominal Bore | 300 | mm
Outfall Pipework - River | DWW - Dirty Wash Water Handling | 1 | New | 9963.1403 | Length | 2 | m
[5 empty] | Diameter | 150 | mm
| Total asset costs |  |  | 7793800.4584
| Site wide Electrical Distribution |  |  | 448143.5264
| Are access amendments required at the site to enable the works to be carried out? |  |  | 84548.4563
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 120396.1902
| Does the solution need modelling prior to delivery? |  |  | 30663.5356
| Does the solution require an extensive planning effort? |  |  | 1102593.4447
| Does the statutory power supply need upgrading? |  |  | 110799.6782
| Is an Environmental Impact Assessment (EIA) report required? |  |  | 173080.8237
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 211302.9496
| Total Location Factors (land purchase , power upgrade, Extensive planning , modelling, EIA) |  |  | 1833385.0782
| On Cost |  |  | 3981905.0838
| Total project CAPEX cost |  |  | 14057234.1467
INVESTMENT_CODE | INVESTMENT_NAME | ASSET_TYPE_CODE | Number of tanks | Volume of media (m3) per tanks | Total Media (m3) | Unit rate | ASSET_COST | ON_COST | Total CAPEX costs
I039910 | GAC Virgin Media Upgrade - Branston Booths PFAS | 13002 | 5 | 20 | 100 | 1993.46 | 199346 | 53205.4474 | 252551.4474
I040027 | GAC Virgin Media Upgrade - Alton PFAS | 13002 | 8 | 38 | 304 | 1993.46 | 606011.84 | 161744.5601 | 767756.4001
I040029 | GAC Virgin Media Upgrade - Ardleigh PFAS | 13002 | 5 | 100 | 500 | 1993.46 | 996730 | 266027.237 | 1262757.237
I040030 | GAC Virgin Media Upgrade - Beck Row PFAS | 13002 | 5 | 37 | 185 | 1993.46 | 368790.1 | 98430.0777 | 467220.1777
I040031 | GAC Virgin Media Upgrade - Grafham PFAS | 13002 | 16 | 258 | 4128 | 1993.46 | 8229002.88 | 2196320.8687 | 10425323.7487
I040032 | GAC Virgin Media Upgrade - Clapham PFAS | 13002 | 6 | 144 | 864 | 1993.46 | 1722349.44 | 459695.0655 | 2182044.5055
I040033 | PR24 GAC Virgin Media Upgrade - Covenham PFAS | 13002 | 6 | 135 | 810 | 1993.46 | 1614702.6 | 430964.1239 | 2045666.7239
I040034 | GAC Virgin Media Upgrade - Elsham PFAS | 13002 | 6 | 104 | 624 | 1993.46 | 1243919.04 | 332001.9918 | 1575921.0318
I040035 | GAC Virgin Media Upgrade - Etton PFAS | 13002 | 4 | 20 | 80 | 1993.46 | 159476.8 | 42564.3579 | 202041.1579
I040036 | GAC Virgin Media Upgrade - Hall PGAC PFAS | 13002 | 5 | 54.4 | 272 | 1993.46 | 542221.12 | 266034.8276 | 1262793.2676
I040037 | GAC Virgin Media Upgrade - Heigham PFAS | 13002 | 8 | 146 | 1168 | 1993.46 | 2328361.28 | 621439.6256 | 2949800.9056
I040038 | GAC Virgin Media Upgrade - Marham PFAS | 13002 | 9 | 50 | 450 | 1993.46 | 897057 | 239424.5133 | 1136481.5133
I040039 | GAC Virgin Media Upgrade - Morcott PFAS | 13002 | 8 | 180 | 1440 | 1993.46 | 2870582.4 | 766158.4426 | 3636740.8426
I040041 | GAC Virgin Media Upgrade - Thorpe-Mousehold PFAS | 13002 | 5 | 40 | 200 | 1993.46 | 398692 | 106410.8948 | 505102.8948
I040042 | GAC Virgin Media Upgrade - Pitsford PFAS | 13002 | 7 | 100 | 700 | 1993.46 | 1395422 | 372438.1318 | 1767860.1318
I040043 | GAC Virgin Media Upgrade - Ravensthorpe PFAS | 13002 | 4 | 30 | 120 | 1993.46 | 239215.2 | 63846.5369 | 303061.7369
I040044 | GAC Virgin Media Upgrade - Saltersford PFAS | 13002 | 6 | 58 | 348 | 1993.46 | 693724.08 | 185154.957 | 878879.037
I040045 | GAC Virgin Media Upgrade - Stoke Ferry PFAS | 13002 | 5 | 50 | 250 | 1993.46 | 498365 | 133013.6185 | 631378.6185
I040046 | GAC Virgin Media Upgrade - Watton PFAS | 13002 | 3 | 20 | 60 | 1993.46 | 119607.6 | 31923.2684 | 151530.8684
I040047 | GAC Virgin Media Upgrade - Wing PFAS | 13002 | 9 | 360 | 3240 | 1993.46 | 6458810.4 | 1723856.4958 | 8182666.8958
I040048 | GAC Virgin Media Upgrade - Hall RGAC PFAS | 13002 | 6 | 72 | 432 | 1993.46 | 861174.72 | 229847.5328 | 1091022.2528
[5 empty] | 16275 |  |  |  | 41678601.3951
Unit cost Build up
| Supplier | Type | Unit rate £/m3 ( inlc Haulage+labour+plant +material) | Revoval and disposal (Incl Labour+Plant ) | Labour+Plant +prelims | Total cost , per supplier
| Chemviron | Virgin - programme sites | 1879.382 | 375.9998 |  | 2255.3818
| Carbon Link T/A CPL | Virgin - programme sites | 1695.1088 | 375.9998 |  | 2071.1086
| Norit | Virgin - programme sites | 1277.8934 | 375.9998 |  | 1653.8932
[5 empty] | Average cost /m3 | 1993.4612
For the calculation of the Unit rate we have seek the cost of three of our Framework suppliers and use the avergae of these in our calculation.
as reference in Ref - OFW-OBQ-ANH-171
*For ‘PFAS Virgin GAC Replacement – multiple sites’, the unit rate also includes
the costs for disposal of the removed GAC media. The cost for removing and
disposing the media is £376 per m3. This rate is based on the assumption this
will be accepted to landfill rather than having to be treated due to
DWI Reference Scheme Name GAC Media
contamination. We note the uncertainty relating to disposal costs of GAC media.
Our requested allowance and associated disposal costs assume that GAC media
will be accepted at landfill. There is a good probability of the reclassification of
GAC media as hazardous waste within AMP8, requiring additional treatment and
presenting a significant cost pressure in this eventuality.
Please note that the costs presented here and within our PR24 PFAS Investment
Summary do not include a cost uplift to reflect changes in the current market
rate for GAC media since business plan submission. Given current market
activity, we anticipate that demand for GAC media will increase drastically over
the course of AMP8 beyond market availability. As such, we recognise that there
is an intrinsic inflation risk that is not currently captured within our AMP8 PFAS
requested allowance. We set out within our enhancement strategy (ANH26,
section 1.2.2) why replacement of existing GAC media with virgin carbon was
chosen as the selected option at our very high-risk sites despite this
uncertainty

## Increased FFT
Investment ID | I034010 |  |  |  |  | the cost show are total costs including Labour, Plant, materials and prelims, Location factors and On costs
Investment Title | Sawston WRC U_IMP5
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of measurement
Biodiversity Net Gain | SS - Site Services | 1 | New | 6900 | Biodiversity Units | 0.23
Landscaping | SS - Site Services | 1 | New | 8296.5083 | Area | 100 | (m2)
Biofilter Tanks - M&E | 2E - Secondary Treatment | 1 | New | 936191.379 | Total Volume | 800 | (m3)
Chamber | PSM - Primary Settlement | 1 | Refurbishment | 34550.6727 | Chamber Use | Distribution
[5 empty] | Refurbishment Scope | Minor Refurbishment
[5 empty] | Volume | 20 | (m3)
Rigid Pipework | SBS - Site Services | 1 | New | 14302.2 | Usage | Process
[5 empty] | Filter Tank Shape | Circular
[5 empty] | Length | 20 | (m)
[5 empty] | Diameter | 400 | (mm)
Footpath | SBS - Site Services | 1 | New | 1574.0769 | Area | 10 | (m2)
Road | SBS - Site Services | 1 | New | 5650.7177 | Area | 20 | (m2)
[5 empty] | Road Type | Site Road
Total Asset Costs |  | 1007465.55
Group Adjustments |  | 3011
Site Wide Electrical Distribution |  | 58102.4
Total Location Factors |  | 73927.17
On Cost |  | 365058.22
Subtotal |  | 1507564.34
Investment ID | I034016
Investment Title | Wymondham WRC U_IMP5
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of measurement
Biodiversity Net Gain | SS - Site Services | 1 | New | 6900 | Biodiversity Units | 0.23
Landscaping | SS - Site Services | 1 | New | 17728.9882 | Area | 300 | m2
Telemetry Outstation | TEL - Telemetry | 1 | New | 5122.35 | Type of Telemetry Outstation | MM4
TSFR Flowmeter - Final Effluent | WYMOST-2K-FED-PM01-TSF001 |  | Replacement | 4372.5553 | Namecode | Tsfr Flowmeter
Rotary Valve | PUM - Inter-Process Pumping | 2 | New | 15330.244 | Nominal Bore | 400 | mm
BAF Plant <#2> | 2M - Full Treatment Process Units | 4 | New | 3858655.36 | Flow | 1548 | (m3/d)
Final Tanks, Circular - Civil | 2E - Secondary Treatment | 1 | New | 466770.3029 | Surface Area | 201 | (m2)
[5 empty] | Total Volume | 473 | (m3)
Final Tanks Scrapers, Circular - M&E | 2E - Secondary Treatment | 1 | New | 399728.1256 | Surface Area | 262 | (m2)
[5 empty] | Total Volume | 757 | (m3)
Aeration, Fine Bubble Diffusers | 2D - Primary Treatment | 1 | New | 3088363.4046 | Total Volume | 9000 | (m3)
Aeration Tanks, Rectangular - Civil | 2D - Primary Treatment | 1 | New | 1697853.4537 | Total Volume | 9000 | (m3)
Inlet Works STW All-in M&E | 2C - Preliminary Treatment | 1 | New | 576518.8077 | Flow | 6696 | (m3/d)
Inlet Works - Civil | 2C - Preliminary Treatment | 1 | New | 127542.4933 | Flow | 6696 | (m3/d)
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 2 | New | 1012298 | Total Installed Power (inc standby) | 120 | kW
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 2 | New | 148082.8843 | Total Installed Power (inc standby) | 120 | kW
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 17874.9683 | Length | 15 | m
[5 empty] | Diameter | 400 | mm
[5 empty] | Usage | Rising Main Pipework
Rigid Pipework <#2> | PUM - Inter-Process Pumping | 1 | New | 117993.15 | Length | 165 | m
[5 empty] | Diameter | 400 | mm
[5 empty] | Usage | Process
Channel - Fe Flume | WYMOST-2K-FED-IQ01-CHN001 |  | Replacement | 23018.4142 | Cross Sectional Area | 1.03 | m2
[5 empty] | Length | 6 | m
Channel | STH - Storm Handling | 1 | New | 12969.6687 | Cross Sectional Area | 4 | m2
[5 empty] | Length | 2 | m
Footpath | SBS - Site Services | 1 | New | 6773.8822 | Area | 70 | m2
Road | SBS - Site Services | 1 | New | 5650.7177 | Area | 20 | m2
[5 empty] | Road Type | Site Road
Total Asset Costs | 11609547.77
Group Adjustments | 3011
Site Wide Electrical Distribution | 667722.13
Total Location Factors | 2681048.13
On Cost | 4620162.43
Subtotal | 19581491.46
Investment ID | I043956
Investment Title | DD Little Bytham UIMP5
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Activity Type | Value | Unit of measurement
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1
Landscaping | SS - Site Services | 1 | New | 17728.9882 | Area | 300 | m2
Roads | SS - Site Services | 1 | New | 44277.8057 | Area | 300 | m3
Kiosks | SS - Site Services | 1 | New | 104255.0316 | Area | 40 | m4
[5 empty] | Security Level | Low
Direct Online Starter | SST - Sludge Storage | 1 | New | 6377.6087 | Installed Power | 2 | kW
[5 empty] | Starter Location | Starter
Sludge Mixers - M&E | 2F - Sludge Handling | 1 | New | 72683.8796 | Total Volume | 60 | m3
Sludge Mixers - M&E <#2> | 2F - Sludge Handling | 1 | New | 72683.8796 | Total Volume | 60 | m3
Sludge Drum Thickener - M&E | 2F - Sludge Handling | 1 | New | 419647.21 | Production | 30 | TDS/year
Sludge Tanks, Pre-Fabricated, Circular - Civil | 2F - Sludge Handling | 1 | New | 222865.8623 | Total Volume | 60 | m3
Sludge Tanks, Pre-Fabricated, Circular - Civil <#2> | 2F - Sludge Handling | 1 | New | 222865.8623 | Total Volume | 60 | m3
Final Tanks, Circular - Civil | 2E - Secondary Treatment | 2 | New | 812328.4663 | Total Volume | 239 | m3
[5 empty] | Surface Area | 80 | m2
Final Tanks Scrapers, Circular - M&E | 2E - Secondary Treatment | 2 | New | 438209.4192 | Total Volume | 239 | m3
[5 empty] | Surface Area | 80 | m2
Aerators, Horizontal Shaft Surface | 2E - Secondary Treatment | 1 | New | 666624.0131 | Total Volume | 672 | m3
Aeration Tanks, Rectangular - Civil | 2E - Secondary Treatment | 1 | New | 557977.8391 | Total Volume | 672 | m3
Inlet Works STW All-in M&E | 2C - Preliminary Treatment | 1 | New | 520858.9072 | Flow | 5184 | m3/d
Inlet Works - Civil | 2C - Preliminary Treatment | 1 | New | 114476.3979 | Flow | 5184 | m3/d
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 160914.75 | Total Installed Power (inc standby) | 24.5 | kW
Prop (Blade) Mixer | SST - Sludge Storage | 2 | New | 15514.3423 | Mixer Use (namecode) | Aeration Mixer
[5 empty] | Installed Power | 2 | kW
Round Tank (Flatfloor) <#2> | AES - Aeartion (Secondary) | 1 | New | 114316.8752 | Tank Use (Namecode) | Balancing Tank
[5 empty] | Volume | 159 | m3
Rigid Pipework | SBS - Site Services | 1 | New | 26811 | Usage | Process
[5 empty] | Length | 50 | m
[5 empty] | Diameter | 250 | mm
Rigid Pipework <#2> | SBS - Site Services | 1 | New | 11917 | Usage | Process
[5 empty] | Length | 20 | m
[5 empty] | Diameter | 300 | mm
Rigid Pipework <#4> | SBS - Site Services | 1 | New | 5958.5 | Usage | Process
[5 empty] | Length | 10 | m
[5 empty] | Diameter | 300 | mm
Rigid Pipework <#5> | SBS - Site Services | 1 | New | 35751 | Usage | Process
[5 empty] | Length | 60 | m
[5 empty] | Diameter | 300 | mm
Rigid Pipework <#6> | SBS - Site Services | 1 | New | 12508.8 | Usage | Process
[5 empty] | Length | 30 | m
[5 empty] | Diameter | 150 | mm
Rigid Pipework <#7> | SBS - Site Services | 1 | New | 4169.6 | Usage | Process
[5 empty] | Length | 10 | m
[5 empty] | Diameter | 150 | mm
Rigid Pipework <#8> | SBS - Site Services | 1 | New | 29792.5 | Usage | Process
[5 empty] | Length | 50 | m
[5 empty] | Diameter | 300 | mm
Cabling Ducting | SGN - Standby Generation | 1 | New | 58417.9295 | Length | 300 | m
[5 empty] | Type of Ducting | Up to 6 Ways
Total Asset Costs | 4783576.51
Group Adjustments | 6884.1
Site Wide Electrical Distribution | 275451.49
Total Location Factors | 292309.73
On Cost | 1667686.95
Subtotal | 7025908.77

## Microbiological Summary
|  | the cost show are total costs including Labour, Plant, materials and prelims, Location factors and On costs | [14 empty] | Bathing |  |  | Storm Overflow
[17 empty] | CAPEX AMP7/8 |  | OPEX AMP8 | CAPEX AMP7/8 | OPEX AMP8 | OPEX ( Annual) | CAPEX Maintenance |  | CWW3.90 |  |  |  | CWW3.24 and CWW3.25
No. | C55 ID | Site | Population Equiv.(inc growth where applicable) | Plant Type | Discharge Consent Standards | Phosphorous Removal | Dry Weather Flow (m3/d) | Full Flow to Treatment (and where applicable growth) (m3/d) | l/s | Stantec design flow L/s ( 3x DWF) | Comments on existing issues/performance | Average SS values in effluent | UV Target Dose mJ/cm2 | Recommended solution | Obligation date | Sludge tank | 52.16 - Quality - NEP UV Dinfection (or similar) - ninf - Sewage Treatment 52.51 - Quality - Bathing Waters - Sewage Treatment |  |  | 99.40 - CWW353F - Storm Overflow sewer flow management and control WINEP 42.42 - Quality - CSO – inf - Sewage |  |  | BIC 55.00 - Maint. - Sewage Treatment Works - Civil - USE TO ALLOCATED AMP7 IN BASE |  | AMP7 CAPEX | AMP8 CAPEX | AMP9 CAPEX | AMP8 OPEX | AMP7 CAPEX | AMP8 CAPEX | AMP8 OPEX
1 | I031443 | King's Lynn STC Disinfection **Multidriver scheme, only 84% is allocated in CWW3.90 lines** | 90000 | Large Activated Sludge Plant and Sludge Treatment Centre | UWWTD COD 125mg/l UT 250mg/l Or 75% removal | None and none planned | 21600 | 71280 | 825 | 750 | Good permeance - but has fine solids in the final effluent. Biosolids Treatment Hub advanced digestion with Monsal enzymic hydrolysis up front of the digesters. Design Throughput = 19,000 tDS/y. | 15 mg/L | 30 | Extend existing ASP to increase sludge age/possible pre trade treatment /sludge liquor treatment/TRS +UV | 2027-07-01 |  | 48554306.892 | 0.84 | 3626655.963 | 9248439.408 | 690791.612 | 1726979.03 |  |  | 0.097276 | 48.5407 |  | 4.5046 | 0.018529 | 9.2458 | 0.51747
2 | I031886 | Boston WRC Disinfection **Multidriver scheme, only 56% is allocated in CWW3.90 lines** | 50000 | Filter Works with Storm Tanks | 70SS, 35BOD, no Ammonia | None and none planned | 10000 | 33000 | 381.9444 | 347.2222 | Existing Storm Storage is located at the TPS (offsite). Planned increased Storm Storage in AMP8. | 30 mg/L | 30 | Add TSR+UV | 2027-07-01 | Silver Assessment document 100 m3/d and 7 days of storage to cover weekends (as per MAS) = 700 m3. | 13654285.1032 | 0.56 | 1394026.312 | 10728366.8668 | 1095306.388 | 995733.08 |  |  | 0.090975 | 13.6932 |  | 1.2616 | 0.071481 | 10.7589 | 0.74402
3 | I033697 | Maldon WRC MALDST Disinfection **Multidriver scheme, only 80% is allocated in CWW3.90 lines** | 32000 | Activated Sludge Plant and Storm Tanks | 25SS, 18BOD, no Ammonia | None and none planned | 6800 | 22440 | 259.7222 | 236.1111 | Storm Tank being planned as a late AMP7 Installation (PR19). Planned AMP8 IMP4 scheme for Storm Spill reduction to 10 per annum and IMP5 scheme for CSO Screens. | 10mg/L | 40 | Expansion of ASP + UV | 2030-04-01 | Gold Assessment document 104 m3/d and 7 days of storage to cover weekends (as per MAS) = 728 m3. | 26255185.76 | 0.8 |  | 6563796.44 |  | 932039.25 |  |  | 0 | 26.2552 |  | 0.83513 | 0 | 6.5638 | 0.12945
4 | I031905 | Woodbridge WRC WOODST Disinfection | 19000 | Filter Works with Storm Tanks | 70SS, 35BOD, no Ammonia | None and none planned | 4800 | 15840 | 183.3333 | 166.6667 |  | 25mg/L | 20 | Upgrade to ASP + UV | 2027-04-01 | Silver Assessment document 36 m3/d and 7 days of storage to cover weekends (as per MAS) = 252 m3. | 23071034.85 | 1 | 1716768.575 |  |  | 686707.43 |  |  | 0 | 23.071 |  | 0.80577
5 | I040840 | Sudbury WRC SUDBST Disinfection **Multidriver scheme, only 63% is allocated in CWW3.90 lines** | 15000 | Filter Works with Tertiary Nitrification and Storm Tanks | 50SS, 25BOD, 8NH3, 2P | 0.5mg/l Planned AMP8 | 3441 | 11356 | 131.4352 | 119.4792 |  | 12 mg/L | 40 | Upgrade with long sludge age ASP + UV | 2030-04-01 | Sudbury similar size to Woodbridge = 38 m3/day * 7 days storage = 266 m3. | 15144719.814 | 0.63 |  | 8894517.986 |  | 739120.68 |  |  | 0 | 15.1736 |  | 0.14528 | 0 | 8.9115 | 0.053242
6 | I040818 | Manningtree WRC MANNST Disinfection **Multidriver scheme, only 84% is allocated in CWW3.90 lines** | 12000 | Filter Works with Storm Tanks | 70SS, 50BOD, 20NH3 | None and none planned | 3000 | 9900 | 114.5833 | 104.1667 |  | 20 mg/L | 40 | Upgrade with long sludge age ASP + UV | 2030-04-01 | Silver Assessment document 24 m3/d and 7 days of storage to cover weekends (as per MAS) = 168 m3. | 14631371.454 | 0.84 |  | 2786927.896 |  | 557129.54 |  |  | 0 | 14.6314 |  | 0.16207 | 0 | 2.7869 | 0.021382
7 | I040871 | Oakham WRC OAKHST Disinfection **Multidriver scheme, only 84% is allocated in CWW3.90lines** | 12000 | Filter Works and MBBR for load removal with Storm Tanks | 60SS, 40BOD, 20NH3, 2P | 0.5mg/l Planned AMP8 | 2962 | 9775 | 113.1366 | 102.8472 | Site is getting a storm tank here under SOAF currently for 40 spills. Lots of issues with finding space as available area is quite wooded (Environmental/badgers). Site receives lots of infiltration from catchment and has issues with returns/balancing; flow control throughout works poor/hard | 25 mg/L | 20 | Existing treatment + UV | 2030-04-01 |  | 5598233.1636 | 0.84 |  | 1066330.1264 |  | 243309.11 |  |  | 0 | 5.4214 | 0.21 | 0.064341 | 0 | 1.0326 | 0.0092596
8 | I040852 | Haslingfield WRC HASLST Disinfection **Multidriver scheme, only 70% is allocated in CWW3.90 lines** | 10000 | Split treatment Filter Works and Oxidation Ditch with Storm Tanks | 60SS, 30BOD, 10NH3, 2P | 1mg/l Planned AMP8 | 2250 | 7425 | 85.9375 | 78.125 |  | 16 mg/L | 40 | Upgrade to ASP + UV | 2030-04-01 | Haslingfield preo-rata with Woodbridge= 1000*38/19000=20 m3/d times 7 days= 140 m3 | 6144781.485 | 0.5 |  | 6144781.485 |  | 435858.94 |  |  | 0 | 8.6027 |  | 0.10737 | 0 | 3.6869 | 0.032388
9 | I031906 | Melton WRC MELTST Disinfection | 6300 | Filter Works | 40SS, 25BOD, no Ammonia | None and none planned | 1257 | 4148 | 48.0093 | 43.6458 | AMP8 scheme allows for Storm Storage | 15 mg/L | 20 | Existing treatment+UV | 2027-04-01 |  | 5176561.83 | 1 | 514260.075 |  |  | 205704.03 |  |  | 0 | 5.1766 |  | 0.66851 | 0 | 0 | 0
10 | I031762 | Southwold WRC Disinfection **Multidriver scheme, only 60% is allocated in CWW3.90 lines** | 5000 | Filter Works with Storm Tanks | 120SS, 100BOD, no Ammonia | None and none planned | 1800 | 5940 | 68.75 | 62.5 | Installed additional Storm Tank in Sept 2021. Currently dosing PFA for disinfection trial. | 40 mg/L | 20 | Upgrade to ASP + UV +1 PST | 2030-04-01 | Silver Assessment document 16 m3/d and 7 days of storage to cover weekends (as per MAS) = 112 m3. | 10419753.27 | 0.6 |  | 2083950.654 |  | 420465.75 | 4862551.526 |  | 0 | 10.4198 |  | 0.2608 | 0 | 2.084 | 0.027841
11 | I031837 | Tollesbury WRC Disinfection **Multidriver scheme, only 61% is allocated in CWW3.90 lines** | 3000 | Filter Works with Storm Tanks | 40SS, 30BOD, no Ammonia | None and none planned | 600 | 1980 | 22.9167 | 20.8333 | Planned AMP8 IMP4 scheme for Storm Spill reduction to 10 per annum | 15 mg/L | 40 | Upgrade to ASP +TSR+ UV | 2030-04-01 | Silver Assessment document 17 m3/d and 7 days of storage to cover weekends (as per MAS) = 119 m3. | 7372131.6797 | 0.61 |  | 4713330.0903 |  | 308502.9 |  |  | 0 | 6.6736 | 1.145 | 0.032454 | 0 | 4.2667 | 0.012268
12 | I031776 | Easton WRC ESTNST Disinfection **Multidriver scheme, only 96% is allocated in CWW3.90 lines** | 210 | Small Aeration tank & settlement No Inlet Works | 30SS, 20BOD, no Ammonia | None and none planned | 28 | 93 | 1.0764 | 0.97222 | AMP8 scheme allows for Storm Storage | 10 mg/L |  | Pump away no change in existing process | 2030-04-01 |  | 3707554.5504 | 0.96 |  | 154481.4396 |  | 21528.76 |  |  | 0 | 3.7076 |  | 0.024818 | 0 | 0.15448 | 0.00046621
13 | I034033 | Paglesham WRC Shellfish Beds | [11 empty] | Paglesham WRC Shellfish Beds Tertiary Lagoon | 2027-07-01 | Paglesham WRC Shellfish Beds Tertiary Lagoon | Paglesham WRC Shellfish Beds Tertiary Lagoon | Paglesham WRC Shellfish Beds Tertiary Lagoon | Paglesham WRC Shellfish Beds Tertiary Lagoon | Paglesham WRC Shellfish Beds Tertiary Lagoon | Paglesham WRC Shellfish Beds Tertiary Lagoon | Paglesham WRC Shellfish Beds Tertiary Lagoon | Paglesham WRC Shellfish Beds Tertiary Lagoon | Paglesham WRC Shellfish Beds Tertiary Lagoon | 0 | 0.48302 |  | 0.02424
14 | I040841 | River Stour MANNST BW Investigation | [11 empty] | River Stour Manningtree Bathing Water Study | 2027-05-01 | River Stour Manningtree Bathing Water Study | River Stour Manningtree Bathing Water Study | River Stour Manningtree Bathing Water Study | River Stour Manningtree Bathing Water Study | River Stour Manningtree Bathing Water Study | River Stour Manningtree Bathing Water Study | River Stour Manningtree Bathing Water Study | River Stour Manningtree Bathing Water Study | River Stour Manningtree Bathing Water Study | 0 | 0.36624 |  | 0
15 | I040842 | River Stour Sudbury BW Investigation | [11 empty] | River Stour Sudbury Bathing Water Study | 2027-05-01 | River Stour Sudbury Bathing Water Study | River Stour Sudbury Bathing Water Study | River Stour Sudbury Bathing Water Study | River Stour Sudbury Bathing Water Study | River Stour Sudbury Bathing Water Study | River Stour Sudbury Bathing Water Study | River Stour Sudbury Bathing Water Study | River Stour Sudbury Bathing Water Study | River Stour Sudbury Bathing Water Study | 0 | 0.35903 |  | 0
16 | I040849 | River Deben Bathing Water Investigation | [11 empty] | River Deben Bathing Water Study | 2027-05-01 | River Deben Bathing Water Study | River Deben Bathing Water Study | River Deben Bathing Water Study | River Deben Bathing Water Study | River Deben Bathing Water Study | River Deben Bathing Water Study | River Deben Bathing Water Study | River Deben Bathing Water Study | River Deben Bathing Water Study | 0 | 0.67544 |  | 0
17 | I040853 | River Cam Bathing Water Investigation | [11 empty] | River Cam Bathing Water Study | 2027-05-01 | River Cam Bathing Water Study | River Cam Bathing Water Study | River Cam Bathing Water Study | River Cam Bathing Water Study | River Cam Bathing Water Study | River Cam Bathing Water Study | River Cam Bathing Water Study | River Cam Bathing Water Study | River Cam Bathing Water Study | 0 | 0.50334 |  | 0
18 | I040854 | Rutland Water BW Investigation | [11 empty] | Rutland Water Bathing Water Study | 2027-05-01 | Rutland Water Bathing Water Study | Rutland Water Bathing Water Study | Rutland Water Bathing Water Study | Rutland Water Bathing Water Study | Rutland Water Bathing Water Study | Rutland Water Bathing Water Study | Rutland Water Bathing Water Study | Rutland Water Bathing Water Study | Rutland Water Bathing Water Study | 0 | 0.4574 |  | 0
19 | I042795 | DD - Shellfish & BW UV Investigations 5 Transition WRCs | [11 empty] | DD - Sampling Lab analysis, Dispersion modelling & Reporting | 2027-01-01 | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | 0 | 1.5555 |  | 0
20 | I042798 | DD - Shellfish & BW UV Investigations 4 WRCs | [11 empty] | DD - Sampling Lab analysis, Dispersion modelling & Reporting | 2027-01-01 | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | 0 | 1.2444 |  | 0
21 | I043709 | DD - Shellfish & BW UV Investigations 3 WRCs | [11 empty] | DD - Sampling Lab analysis, Dispersion modelling & Reporting | 2027-01-01 | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | DD - Sampling Lab analysis, Dispersion modelling & Reporting | 0 | 0.9333 |  | 0
22 | I043897 | DD Sudbury CSOs Stour Bathing Water | [11 empty] | DD Sudbury CSOs Stour Bathing Water 2 No. CSOs spill reduction | 2030-04-01 | DD Sudbury CSOs Stour Bathing Water 2 No. CSOs spill reduction | DD Sudbury CSOs Stour Bathing Water 2 No. CSOs spill reduction | DD Sudbury CSOs Stour Bathing Water 2 No. CSOs spill reduction | DD Sudbury CSOs Stour Bathing Water 2 No. CSOs spill reduction | DD Sudbury CSOs Stour Bathing Water 2 No. CSOs spill reduction | DD Sudbury CSOs Stour Bathing Water 2 No. CSOs spill reduction | DD Sudbury CSOs Stour Bathing Water 2 No. CSOs spill reduction | DD Sudbury CSOs Stour Bathing Water 2 No. CSOs spill reduction | DD Sudbury CSOs Stour Bathing Water 2 No. CSOs spill reduction | 0 | 1.1977 |  | 0.0088202
[17 empty] | TOTEX |  | #VALUE! |  | #VALUE!
[14 empty] | Grand Total ( incl Business rate and sludge) |  |  | TOTEX |  | 35.9209 |  | 17.8262 |  |  |  | 0.18825 | 189.142 |  | 8.9058
[14 empty] | Grand total excluding Business rates and sludge | [10 empty] | 0.18825 | 189.142 | 1.355 | 5.733 | 0.090009 | 49.4917 | 1.5478
[17 empty] | TOTEX |  | #VALUE! |  | #VALUE!
[17 empty] | TOTEX |  | 33.9434 |  | 3.8294
[17 empty] | Increase |  | #VALUE! |  | #VALUE!

## Microbiological Cost Breakdown
[5 empty] | 191751455.6578 |  | the cost show are total costs including Labour, Plant, materials and prelims, Location factors and On costs
|  | Investment ID | I031443
|  | Investment Title | King's Lynn STC Disinfection
| Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
|  | UV Disinfection - M&E | 2H - Tertiary Treatment | 1 | New | 3890498.762 | Flow | 71280 | m3/d
[7 empty] | UV Dose Required | 30 | mJ/cm2
|  | UV Disinfection - Civil | 2H - Tertiary Treatment | 1 | New | 328041.2871 | Flow | 71280 | m3/d
[7 empty] | UV Dose Required | 30 | mJ/cm2
|  | Rigid Pipework - Rising Main Pipework | TES - Tertiary Settlement | 1 | New | 333563.0061 | Length | 200 | m
[7 empty] | Diameter | 1000 | mm
|  | Standby Generation | SS - Site Services | 1 | New | 311176.4701 | Total Installed Power | 476 | kW
|  | Sewer - Manhole | 03 - AW Water Recycling Infra | 1 | New | 14690.5 | Diameter pipe connected | 250 | mm
[7 empty] | Depth | 5 | m
|  | Sewer - Rising Main | 03 - AW Water Recycling Infra | 1 | New | 18546.929 | Diameter | 225 | mm
[7 empty] | Length in Grassland | 30 | m
[7 empty] | Length in 3/4 Reinstatment | 15
[7 empty] | Depth | 1.5 | m
|  | Collection Storage - Offline | 03 - AW Water Recycling Infra | 1 | New | 1872704.3518 | Storage Volume | 1660 | m3
[7 empty] | Fencing length | 60 | m
[7 empty] | Landscaping Area | 100 | m
[7 empty] | Road Length | 30 | m
[7 empty] | Telemetry | 1 | number
|  | Rigid Pipework <#2> Process | TUV - UV Treatment | 1 | New | 256364 | Length | 100 | m
[7 empty] | Diameter | 1950 | mm
|  | Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 64387.8804 | Total Installed Power (inc standby) | 60 | kW
|  | Pumps, Supernatant - M&E | 2A - Catchment Pumping | 1 | New | 234239.0929 | Total Installed Power (inc standby) | 60 | kW
|  | Sewer - Gravity | 03 - AW Water Recycling Infra | 1 | New | 59584.6264 | Diameter | 300 | mm
[7 empty] | Length in 3/4 Reinstatment | 30 | m
[7 empty] | Depth | 4 | m
[7 empty] | Manholes | 1 | Number
|  | Telemetry | SS - Site Services | 1 | New | 13643.0426 | Units | 1 | number
|  | Biodiversity Net Gain | SS - Site Services | 1 | New | 150000 | Units | 5 | number
|  | Landscaping | SS - Site Services | 1 | New | 8296.5083 | Area | 100 | m2
|  | Final Tanks, Circular - Civil | 2E - Secondary Treatment | 4 | New | 5373945.2464 | Total Volume | 3858 | m3
|  | Final Tanks Scrapers, Circular - M&E | 2E - Secondary Treatment | 4 | New | 3738201.283 | Total Volume | 3858 | m3
|  | Aeration, Fine Bubble Diffusers | 2E - Secondary Treatment | 6 | New | 7272561.9548 | Total Volume | 2204 | m3
|  | Aeration Tanks, Rectangular - Civil | 2E - Secondary Treatment | 6 | New | 5571831.9763 | Total Volume | 2204 | m3
|  | Roads | SS - Site Services | 1 | New | 68774.2596 | Area | 500 | m2
|  | Storm Tanks, Circular - M&E | 2C - Preliminary Treatment | 2 | New | 1644022.3327 | Total Volume | 3858 | m3
|  | Storm Tanks, Circular - Civil | 2C - Preliminary Treatment | 2 | New | 683541.6545 | Total Volume | 3858 | m3
|  | Rigid Pipework <#3> Process | STH - Storm Handling | 1 | New | 558466.2 | Length | 150 | m
[7 empty] | Diameter | 900 | mm
|  | Rigid Pipework <#4> Process | AES - Aeartion (Secondary) | 1 | New | 558466.2 | Length | 150 | m
[7 empty] | Diameter | 900 | mm
|  | Dosing Unit | CET - Centrate Treatment | 1 | New | 231952.0027 | Flow to be Treated | 71280 | m3/d
[7 empty] | Sludge Production | 7000 | TDS/yr
|  | Continuous Sand Filtration | 2H - Tertiary Treatment | 3 | New | 3724864.2059 | Flow | 6333 | m3/d
|  | Transformer | ELE - Electrical Distribution | 1 | New | 39520.3764 | Capacity | 476 | kW
|  | PLC | SBS - Site Services | 1 | New | 10167.5988 | In/Out Cards (number) | 1 | number
|  | Transformer Starter | ELE - Electrical Distribution | 1 | New | 42923.8779 | Installed Power | 476 | kW
|  | Steps | BLD - BUILDING | 1 | New | 3920.4395 | Height | 1 | m
|  | Platform | BLD - BUILDING | 1 | New | 26986.3653 | Area | 10 | m2
|  | Cabling Ducting - up to 12 ways | SBS - Site Services | 1 | New | 199357.8137 | Length | 500 | m
|  | Kiosks - LPBC4 | SS - Site Services | 1 | New | 151132.7098 | Area | 25 | m2
|  | Landscaping <#2> | SS - Site Services | 1 | New | 13395.8042 | Area | 200 | m2
|  | Total Asset direct costs |  |  |  | 37469768.7586
|  | Permit Cost |  |  |  | 9056
|  | Site wide Electrical Distribution at WRC |  |  |  | 2042014.6552
Location Factors
|  |  | Are access amendments required at the site to enable the works to be carried out? |  |  | 374379.7491
|  |  | Are temporary works required to keep the existing plant operational? |  |  | 190265.4178
|  |  | Are the works in a town centre/heavily congested area? |  |  | 109932.25
|  |  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 561066.835
|  |  | Do the works cross other significant infrastructure - rail lines, open water, major roads, medium and high pressure gas lines? |  |  | 47648.4846
|  |  | Does the solution need modelling prior to delivery? |  |  | 80064.3293
|  |  | Does the solution require an extensive planning effort? |  |  | 228981.1988
|  |  | Does the statutory power supply need upgrading? |  |  | 1325363.484
|  |  | Is an Environmental Impact Assessment (EIA) report required? |  |  | 788661.5731
|  |  | Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 948698.8891
|  |  | Does the site have poor ground conditions - does it need piling? |  |  | 52676.1077
|  | Total Location Factor Costs ( access ammendments, temporary works, land purchase modelling, EIA, power upgrade, pilling) |  |  |  | 4707738.3184
|  | On Cost |  |  |  | 13673745.7652
|  | Grand Total CAPEX |  |  |  | 57902323.4974
|  | Investment ID | I031886
|  | Investment Title | Boston WRC Disinfection
| Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
|  | Rigid Pipework - Rising Main Pipework | SWOLST-2A-PUM | 1 | New | 114638.7619 | Length | 110 | m
[7 empty] | Diameter | 300 | mm
|  | Pumping Stations, Interprocess Civils | SWOLST-2A | 1 | New | 60381.2902 | Total Installed Power (inc standby) | 45 | kW
|  | Storm Tanks, Circular - Civil | SWOLST-2C | 6 | New | 1748116.1193 | Total Volume | 2010 | m3
|  | Storm Tanks, Circular M&E | SWOLST-2C | 6 | New | 3045104.4722 | Total Volume | 2010 | m3
|  | UV Disinfection civil | SWOLST-2H | 1 | New | 302024.1145 | Flow | 33000 | m3/d
[7 empty] | UV Dose Required | 30 | mJ/cm2
|  | UV Disinfection (M&E) | SWOLST-2H | 1 | New | 2481833.042 | Flow | 33000 | m3/d
[7 empty] | UV Dose Required | 30 | mJ/cm2
|  | Roads | SWOLST-SS | 1 |  | 24360.7023 | Area | 150 | m2
|  | Boundary Fencing - General | SWOLST-SS | 1 | New | 11715.6856 | Length | 50 | m
|  | Landscaping | SWOLST-SS | 1 | New | 8296.5083 | Area | 100 | m2
|  | Standby Generation | SS - Site Services | 1 | New | 285590.8463 | Total Installed Power | 398 | kW
|  | Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 60381.2902 | Total Installed Power (inc standby) | 45 | kW
|  | Rigid Pipework <#2> Process | TUV - UV Treatment | 1 | New | 83437 | Length | 100 | m
[7 empty] | Diameter | 500 | mm
|  | Pumps, Supernatant - M&E | 2A - Catchment Pumping | 1 | New | 214116.3744 | Total Installed Power (inc standby) | 45 | kW
|  | Biodiversity Net Gain | SS - Site Services | 1 | New | 150000 | Units | 5 | number
|  | Telemetry | SS - Site Services | 1 | New | 13643.0426 | Units | 1 | number
|  | Pumps, Storm - M&E | 2A - Catchment Pumping | 1 | New | 273903.5285 | Total Installed Power (inc standby) | 45 | kW
|  | Continuous Sand Filtration <#2> | 2H - Tertiary Treatment | 4 | New | 5246789.5823 | Flow | 8250 | m3/d
|  | Sludge Mixers - M&E | 2F - Sludge Handling | 1 | New | 176986.1812 | Total Volume | 700 | m3
|  | Sludge Tanks, Pre-Fabricated, Circular | 2F - Sludge Handling | 1 | New | 667588.836 | Total Volume | 700 | m3
|  | Cabling Ducting - up to 12 Ways | ELE - Electrical Distribution | 1 | New | 92828.155 | Length | 210 | m
|  | Transformer | ELE - Electrical Distribution | 1 | New | 35033.5497 | Capacity | 398 | kW
|  | Transformer Starter | ELE - Electrical Distribution | 1 | New | 39988.5668 | Installed Power | 398 | kW
|  | Platform | BLD - BUILDING | 1 | New | 51982.7399 | Area | 20 | m2
|  | Steps | BLD - BUILDING | 1 | New | 3920.4395 | Height | 1 | m
|  | Kiosks - LPBC4 | SS - Site Services | 1 | New | 232078.886 | Area | 40 | m2
|  | PLC | SBS - Site Services | 1 | New | 10167.5988 | In/Out Cards (number) | 1 | number
|  | Total Asset direct costs |  |  |  | 15434907.3135
|  | Permit Cost |  |  |  | 9056
|  | Site wide Electrical Distribution at WRC |  |  |  | 888027.8905
Location Factors
|  |  | Are temporary works required to keep the existing plant operational? |  |  | 1129891.0793
|  |  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 231860.9308
|  |  | Does the site have poor ground conditions - does it need piling? |  |  | 437697.3643
|  |  | Does the solution need modelling prior to delivery? |  |  | 33086.5928
|  |  | Does the solution require an extensive planning effort? |  |  | 94626.5054
|  |  | Does the statutory power supply need upgrading? |  |  | 547706.6045
|  | Total Location Factor Costs ( temporary works, land purchase ,modelling, power upgrade, pilling) |  |  |  | 2474869.0771
|  | On Cost |  |  |  | 5807689.2194
|  | Grand Total CAPEX |  |  |  | 24614549.5005
|  | Investment ID | I033697
|  | Investment Title | Maldon WRC MALDST Disinfection
| Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
|  | UV Disinfection - M&E | 2H - Tertiary Treatment | 1 | New | 2858080.5976 | Flow | 22440 | m3/d
[7 empty] | UV Dose Required | 40 | mJ/cm2
|  | UV Disinfection - Civil | 2H - Tertiary Treatment | 1 | New | 313771.6414 | Flow | 22440 | m3/d
[7 empty] | UV Dose Required | 40 | mJ/cm2
|  | Storm Tanks, Circular - M&E | 2C - Preliminary Treatment | 6 | New | 3045104.4722 | Total Volume | 2010 | m3
|  | Storm Tanks, Circular - Civil | 2C - Preliminary Treatment | 6 | New | 1748116.1193 | Total Volume | 2010 | m3
|  | Rigid Pipework - Rising Main Pipework | PUM - Inter-Process Pumping | 1 | New | 3217.827 | Length | 10 | m
[7 empty] | Diameter | 75 | mm
|  | Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 60381.2902 | Total Installed Power (inc standby) | 45 | kW
|  | Rigid Pipework <#2> Rising Main Pipework | PUM - Inter-Process Pumping | 1 | New | 13639.5326 | Length | 20 | m
[7 empty] | Diameter | 150 | mm
|  | Standby Generation | SS - Site Services | 1 | New | 258387.444 | Total Installed Power | 307 | kW
|  | Rigid Pipework <#3> Process | TUV - UV Treatment | 1 | New | 26811 | Length | 50 | m
[7 empty] | Diameter | 250 | mm
|  | Pumping Stations, Interprocess - Civil <#2> | 2A - Catchment Pumping | 1 | New | 60381.2902 | Total Installed Power (inc standby) | 45 | kW
|  | Pumps, Supernatant - M&E | 2A - Catchment Pumping | 1 | New | 214116.3744 | Total Installed Power (inc standby) | 45 | kW
|  | Biodiversity Net Gain | SS - Site Services | 1 | New | 150000 | Units | 5 | number
|  | Pumps, Storm - M&E | 2A - Catchment Pumping | 1 | New | 273903.5285 | Total Installed Power (inc standby) | 45 | kW
|  | Telemetry | SS - Site Services | 1 | New | 13643.0426 | Units | 1 | number
|  | Landscaping | SS - Site Services | 1 | New | 8296.5083 | Area | 100 | m2
|  | Sludge Mixers - M&E | 2F - Sludge Handling | 1 | New | 178651.3218 | Total Volume | 728 | m3
|  | Sludge Tanks, Pre-Fabricated, Circular - Civil | 2F - Sludge Handling | 1 | New | 687045.5019 | Total Volume | 728 | m3
|  | Rigid Pipework <#4> Process | TUV - UV Treatment | 1 | New | 188607.3 | Length | 100 | m
[7 empty] | Diameter | 450 | mm
|  | Final Tanks, Circular - Civil | 2E - Secondary Treatment | 2 | New | 1275938.9997 | Total Volume | 1134 | m3
|  | Final Tanks Scrapers, Circular - M&E | 2E - Secondary Treatment | 2 | New | 987021.3765 | Total Volume | 1134 | m3
|  | Aeration, Fine Bubble Diffusers | 2E - Secondary Treatment | 2 | New | 4087319.8885 | Total Volume | 5216 | m3
|  | Aeration Tanks, Rectangular - Civil | 2E - Secondary Treatment | 2 | New | 2687376.6863 | Total Volume | 5216 | m3
|  | Rigid Pipework <#5> Process | AES - Aeartion (Secondary) | 2 | New | 377214.6 | Length | 100 | m
[7 empty] | Diameter | 450 | mm
|  | Rigid Pipework <#6> Process | FSM - Final Settlement | 2 | New | 377214.6 | Length | 100 | m
[7 empty] | Diameter | 450 | mm
|  | Rigid Pipework <#7> Process | TES - Tertiary Settlement | 2 | New | 377214.6 | Length | 100 | m
[7 empty] | Diameter | 450 | mm
|  | Cabling Ducting- Up to 12 ways | SBS - Site Services | 1 | New | 127105.1701 | Length | 300 | m
|  | Transformer | SBS - Site Services | 1 | New | 29414.7558 | Capacity | 307 | kW
|  | Transformer Starter | SBS - Site Services | 1 | New | 36083.7353 | Installed Power | 307 | kW
|  | PLC | SBS - Site Services | 1 | New | 10167.5988 | In/Out Cards (number) | 1 | number
|  | Platform | SBS - Site Services | 1 | New | 76279.2881 | Area | 30 | m2
|  | Kiosk - LPCB4 | SBS - Site Services | 1 | New | 124150.6511 | Area | 20 | m2
|  | Steps | SBS - Site Services | 1 | New | 3920.4395 | Height | 1 | m
|  | Landscaping <#2> | SS - Site Services | 1 | New | 8296.5083 | Area | 100 | m2
|  | Total Asset direct costs |  |  |  | 20686873.69
|  | Permit Cost |  |  |  | 9056
|  | Site wide Electrical Distribution at WRC |  |  |  | 1190015.9572
Location Factors
|  |  | Are temporary works required to keep the existing plant operational? |  |  | 1514128.586
|  |  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 310708.9433
|  |  | Does the solution need modelling prior to delivery? |  |  | 44338.2171
|  |  | Does the solution require an extensive planning effort? |  |  | 126805.7598
|  |  | Does the statutory power supply need upgrading? |  |  | 733962.9826
|  |  | Is an Environmental Impact Assessment (EIA) report required? |  |  | 459604.8586
|  | Total Location Factor Costs ( temporary works, land purchase modelling, EIA, power upgrade,) |  |  |  | 3189549.3475
|  | On Cost |  |  |  | 7743487.2049
|  | Grand Total CAPEX |  |  |  | 32818982.1996
|  | Investment ID | I031905
|  | Investment Title | Woodbridge WRC WOODST Disinfection
| Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
|  | UV Disinfection civil <#2> | SWOLST-2H | 1 | New | 277259.6048 | Flow | 15840 | m3/d
[7 empty] | UV Dose Required | 20 | mJ/cm2
|  | UV Disinfection (M&E) <#2> | SWOLST-2H | 1 | New | 1486278.113 | Flow | 15840 | m3/d
[7 empty] | UV Dose Required | 20 | mJ/cm2
|  | Roads | SWOLST-SS | 1 |  | 9449.2627 | Area | 50 | m2
|  | Boundary Fencing- General | SWOLST-SS | 1 | New | 11715.6856 | Length | 50 | m
|  | Washwater Pressure Pipelines | SWOLST-SS | 1 | New | 7596.7251 | Length | 50 | m
|  | Landscaping | SWOLST-SS | 1 | New | 5138.3291 | Area | 50 | m2
|  | Standby Generation | SS - Site Services | 1 | New | 235323.2685 | Total Installed Power | 222 | kW
|  | Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 2 | New | 83946.008 | Total Installed Power (inc standby) | 12 | kW
|  | Rigid Pipework - Process | TUV - UV Treatment | 2 | New | 119170 | Length | 100 | m
[7 empty] | Diameter | 300 | mm
|  | Pumps, Supernatant - M&E | 2A - Catchment Pumping | 1 | New | 160842.7426 | Total Installed Power (inc standby) | 18 | kW
|  | Rigid Pipework <#2> Process | TUV - UV Treatment | 2 | New | 50640.5 | Length | 50 | m
[7 empty] | Diameter | 225 | mm
|  | Biodiversity Net Gain | SS - Site Services | 1 | New | 60000 | Units | 2 | number
|  | Telemetry | SS - Site Services | 1 | New | 27286.0852 | Units | 2 | number
|  | Inlet Works - Civil | 2C - Preliminary Treatment | 1 | New | 183472.0973 | Flow | 15840 | m3/d
|  | Inlet Works STW All-in M&E | 2C - Preliminary Treatment | 1 | New | 811251.2362 | Flow | 15840 | m3/d
|  | Pumps, Storm - M&E | 2A - Catchment Pumping | 1 | New | 154091.6903 | Total Installed Power (inc standby) | 12 | kW
|  | Storm Tanks, Circular - M&E | 2C - Preliminary Treatment | 3 | New | 1522552.2361 | Total Volume | 2010 | m3
|  | Storm Tanks, Circular - Civil | 2C - Preliminary Treatment | 3 | New | 874058.0596 | Total Volume | 2010 | m3
|  | Sludge blanket detector (Digital) | STH - Storm Handling | 6 | New | 98970.0943 | Units | 1 | Number
|  | Sludge Mixers - M&E | 2F - Sludge Handling | 1 | New | 133611.3186 | Total Volume | 252 | m3
|  | Sludge Tanks, Pre-Fabricated, Circular - Civil | 2F - Sludge Handling | 1 | New | 356282.7647 | Total Volume | 252 | m3
|  | Aeration, Fine Bubble Diffusers | 2E - Secondary Treatment | 1 | New | 4976780.8648 | Total Volume | 15840 | m3
|  | Aeration Tanks, Rectangular - Civil | 2E - Secondary Treatment | 1 | New | 2163682.1675 | Total Volume | 15840 | m3
|  | Rigid Pipework <#3> Process | TUV - UV Treatment | 1 | New | 168195.8 | Length | 100 | m
[7 empty] | Diameter | 400 | mm
|  | Rigid Pipework <#4> Process | AES - Aeartion (Secondary) | 1 | New | 168195.8 | Length | 100 | m
[7 empty] | Diameter | 400 | mm
|  | Rigid Pipework <#5> Process | STH - Storm Handling | 1 | New | 209018.8 | Length | 100 | m
[7 empty] | Diameter | 500 | mm
|  | Kiosk -LPCB4 | SBS - Site Services | 1 | New | 178114.7685 | Area | 30 | m2
|  | Cabling Ducting - up to 12 ways | SBS - Site Services | 1 | New | 48280.7032 | Length | 100 | m
|  | Platform | SBS - Site Services | 1 | New | 51982.7399 | Area | 20 | m2
|  | Landscaping <#2> | SBS - Site Services | 1 | New | 48401.2441 | Area | 500 | m2
|  | Transformer | SBS - Site Services | 1 | New | 23646.3755 | Capacity | 222 | kW
|  | Transformer Starter | SBS - Site Services | 1 | New | 31738.6629 | Installed Power | 222 | kW
|  | Steps | SBS - Site Services | 1 | New | 3920.4395 | Height | 1 | m
|  | PLC- process control | SBS - Site Services | 1 | New | 19549.1758 | In/Out Cards (number) | 3 | number
|  | Total Asset direct costs |  |  |  | 14760443.3634
|  | Permit Cost |  |  |  | 9056
|  | Site wide Electrical Distribution at WRC |  |  |  | 849246.21
Location Factors
|  |  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 221735.1726
|  |  | Does the site have poor ground conditions - does it need piling? |  |  | 418582.3815
|  |  | Does the solution need modelling prior to delivery? |  |  | 31641.6455
|  |  | Does the solution require an extensive planning effort? |  |  | 90494.0062
|  |  | Does the statutory power supply need upgrading? |  |  | 523787.3325
|  |  | Is an Environmental Impact Assessment (EIA) report required? |  |  | 327993.6571
|  |  | Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 394551.0073
|  | Total Location Factor Costs ( temporary works, land purchase modelling, EIA, power upgrade,piling, demolition) |  |  |  | 2008785.2025
|  | On Cost |  |  |  | 5443504.0693
|  | Grand Total CAPEX |  |  |  | 23071034.8452
|  | Investment ID | I040840
|  | Investment Title | Sudbury WRC SUDBST Disinfection
| Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
|  | UV Disinfection civil <#2> | SWOLST-2H | 1 | New | 287594.9086 | Flow | 11356 | m3/d
[7 empty] | UV Dose Required | 40 | mJ/cm2
|  | UV Disinfection (M&E) <#2> | SWOLST-2H | 1 | New | 1947252.0863 | Flow | 11356 | m3/d
[7 empty] | UV Dose Required | 40 | mJ/cm2
|  | Roads | SWOLST-SS | 1 |  | 9449.2627 | Area | 50 | m2
|  | Boundary Fencing- General | SWOLST-SS | 1 | New | 11715.6856 | Length | 50 | m
|  | Washwater Pressure Pipelines | SWOLST-SS | 1 | New | 7596.7251 | Length | 50 | m
|  | Landscaping | SWOLST-SS | 1 | New | 5138.3291 | Area | 50 | m2
|  | Standby Generation | SS - Site Services | 1 | New | 237142.2517 | Total Installed Power | 229 | kW
|  | Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 41973.004 | Total Installed Power (inc standby) | 12 | kW
|  | Rigid Pipework- Process | TUV - UV Treatment | 2 | New | 119170 | Length | 100 | m
[7 empty] | Diameter | 300 | mm
|  | Pumps, Supernatant - M&E | 2A - Catchment Pumping | 1 | New | 141716.583 | Total Installed Power (inc standby) | 12 | kW
|  | Rigid Pipework <#2> - Process | TUV - UV Treatment | 2 | New | 50640.5 | Length | 50 | m
[7 empty] | Diameter | 225 | mm
|  | Biodiversity Net Gain | SS - Site Services | 1 | New | 60000 | Units | 2 | number
|  | Telemetry | SS - Site Services | 1 | New | 27286.0852 | Units | 2 | number
|  | Rigid Pipework <#3> Process - DI | STH - Storm Handling | 1 | New | 249841.8 | Length | 100 | m
[7 empty] | Diameter | 600 | mm
|  | Storm Tanks, Circular - M&E | 2C - Preliminary Treatment | 1 | New | 994744.4784 | Total Volume | 4873 | m3
|  | Storm Tanks, Circular - Civil | 2C - Preliminary Treatment | 1 | New | 890276.8811 | Total Volume | 4873 | m3
|  | Sewer - Rising Main | 03 - AW Water Recycling Infra | 1 | New | 22304.5635 | Diameter | 150 | mm
[7 empty] | Length in 3/4 Reinstatment | 50 | m
[7 empty] | Depth | 2 | m
|  | Sewer - Rising Main <#2> | 03 - AW Water Recycling Infra | 1 | New | 17214.0466 | Diameter | 150 | mm
[7 empty] | Length in 2 Reinstatment | 50 | m
[7 empty] | Depth | 2 | m
|  | Sewer - Gravity | 03 - AW Water Recycling Infra | 1 | New | 92103.56 | Diameter | 300 | mm
[7 empty] | Length in 3/4 Reinstatment | 50 | m
[7 empty] | Depth | 4 | m
[7 empty] | Manholes | 1 | Number
|  | Sewer - Gravity <#2> | 03 - AW Water Recycling Infra | 1 | New | 92103.56 | Diameter | 300 | mm
[7 empty] | Length in 3/4 Reinstatment | 50 | m
[7 empty] | Depth | 4 | m
[7 empty] | Manholes | 1 | Number
|  | Collection Storage - Offline | 03 - AW Water Recycling Infra | 1 | New | 746062.6134 | Storage Volume | 500 | m3
[7 empty] | Fencing length | 80 | m
[7 empty] | Landscaping Area | 80 | m
[7 empty] | Road Length | 20 | m
[7 empty] | Telemetry | 1 | number
|  | Collection Storage - Offline <#2> | 03 - AW Water Recycling Infra | 1 | New | 746062.6134 | Storage Volume | 500 | m3
[7 empty] | Fencing length | 80 | m
[7 empty] | Landscaping Area | 80 | m
[7 empty] | Road Length | 20 | m
[7 empty] | Telemetry | 1 | number
|  | Sewer - Rising Main <#3> | 03 - AW Water Recycling Infra | 1 | New | 22304.5635 | Diameter | 150 | mm
[7 empty] | Length in 3/4 Reinstatment | 50 | m
[7 empty] | Depth | 1.5 | m
|  | Sewer - Gravity <#3> | 03 - AW Water Recycling Infra | 1 | New | 92103.56 | Diameter | 300 | mm
[7 empty] | Length in 3/4 Reinstatment | 50 | m
[7 empty] | Depth | 3 | m
[7 empty] | Manholes | 1 | Number
|  | Collection Storage - Offline <#3> | 03 - AW Water Recycling Infra | 1 | New | 746062.6134 | Storage Volume | 500 | m3
[7 empty] | Fencing length | 80 | m
[7 empty] | Landscaping Area | 80 | m
[7 empty] | Road Length | 20 | m
[7 empty] | Telemetry | 1 | number
|  | Sludge blanket detector (Digital) | BLK - Balancing Lakes | 1 | New | 16495.0157 | Units | 1 | Number
|  | Sludge Mixers - M&E | 2G - Sludge Centre | 1 | New | 135906.7773 | Total Volume | 266 | m3
|  | Sludge Tanks, Pre-Fabricated, Circular - Civil | 2F - Sludge Handling | 1 | New | 366011.0805 | Total Volume | 266 | m3
|  | Rigid Pipework <#4> Proces- DI | AES - Aeartion (Secondary) | 1 | New | 147784.3 | Length | 100 | m
[7 empty] | Diameter | 350 | mm
|  | Aeration, Fine Bubble Diffusers | 2E - Secondary Treatment | 1 | New | 3738818.3076 | Total Volume | 11356 | m3
|  | Aeration Tanks, Rectangular - Civil | 2E - Secondary Treatment | 1 | New | 1875896.3083 | Total Volume | 11356 | m3
|  | Final Tanks, Circular - Civil | 2E - Secondary Treatment | 1 | New | 698834.5699 | Total Volume | 1369 | m3
|  | Final Tanks Scrapers, Circular - M&E | 2E - Secondary Treatment | 1 | New | 544440.0805 | Total Volume | 1369 | m3
|  | Cabling Ducting - up to 12 ways | SBS - Site Services | 1 | New | 88922.1413 | Length | 200 | m
|  | Transformer | SBS - Site Services | 1 | New | 24145.8944 | Capacity | 229 | kW
|  | Transformer Starter | SBS - Site Services | 1 | New | 32131.0563 | Installed Power | 229 | kW
|  | Platform | SBS - Site Services | 1 | New | 51982.7399 | Area | 20 | m2
|  | Steps | SBS - Site Services | 1 | New | 3920.4395 | Height | 1 | m
|  | PLC | SBS - Site Services | 1 | New | 10167.5988 | In/Out Cards (number) | 1 | process control
|  | Landscaping <#2> | SS - Site Services | 1 | New | 15629.802 | Area | 250 | m2
|  | Kiosks - LPBC4 | SS - Site Services | 1 | New | 232078.886 | Area | 40 | m2
|  | Total Asset direct costs |  |  |  | 15641025.2726
|  | Permit Cost |  |  |  | 9056
|  | Site wide Electrical Distribution at WRC |  |  |  | 751741.18
Location Factors
|  |  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 232852.3063
|  |  | Does the site have poor ground conditions - does it need piling? |  |  | 439568.8414
|  |  | Does the solution need modelling prior to delivery? |  |  | 33228.0623
|  |  | Does the solution require an extensive planning effort? |  |  | 80104.0611
|  |  | Does the statutory power supply need upgrading? |  |  | 550048.4518
|  |  | Is an Environmental Impact Assessment (EIA) report required? |  |  | 290335.5158
|  |  | Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 349251.1753
|  | Total Location Factor Costs (, land purchase modelling, EIA, power upgrade,piling, demolition) |  |  |  | 1975388.414
|  | On Cost |  |  |  | 5707930.2716
|  | Grand Total CAPEX |  |  |  | 24085141.1382
| Investment ID | I040818
| Investment Title | DD Manningtree WRC MANNST Disinfection
| Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
|  | Rigid Pipework | SWOLST-2A-PUM | 1 | New | 114638.7619 | Length | 110 | m
[7 empty] | Diameter | 300 | mm
|  | UV Disinfection civil | SWOLST-2H | 1 | New | 282591.8341 | Flow (m3/d) | 9900 | m3/d
[7 empty] | UV Dose Required | 40 | mJ/cm2
|  | UV Disinfection (M&E) | SWOLST-2H | 1 | New | 1802391.2285 | Flow (m3/d) | 9900 | m3/d
[7 empty] | UV Dose Required | 40 | mJ/cm2
|  | Roads | SWOLST-SS | 1 | New | 24360.7023 | Area | 150 | m2
|  | Boundary Fencing | SWOLST-SS | 1 | New | 11715.6856 | Length | 50 | m
|  | Washwater Pressure Pipelines | SWOLST-SS | 1 | New | 7596.7251 | Length | 100 | m
|  | Landscaping | SWOLST-SS | 1 | New | 8296.5083 | Area | 100 | m2
|  | Standby Generation | SS - Site Services | 1 | New | 206673.8 | Total Installed Power (inc standby) | 167 | kW
|  | Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 47619.9757 | Total Installed Power (inc standby) | 18 | kW
|  | Rigid Pipework <#2> | TUV - UV Treatment | 1 | New | 59585 | Length | 100 | m
[7 empty] | Diameter | 300 | mm
|  | Pumps, Supernatant - M&E | 2A - Catchment Pumping | 1 | New | 160842.7426 | Total Installed Power (inc standby) | 18 | kW
|  | Biodiversity Net Gain | SS - Site Services | 1 | New | 60000 | Flow (m3/d) | 2 | m3/d
|  | Telemetry | SS - Site Services | 1 | New | 13643.0426 | Quantity | 1 | Number
|  | Storm Tanks, Circular - M&E | 2C - Preliminary Treatment | 1 | New | 994744.4784 | Total Volume (m3) | 4873 | m3
|  | Storm Tanks, Circular - Civil | 2C - Preliminary Treatment | 1 | New | 361880.3179 | Total Volume (m3) | 4873 | m3
|  | Rigid Pipework <#3> | STH - Storm Handling | 1 | New | 124920.9 | Length | 50 | m
[7 empty] | Diameter | 600 | mm
|  | Sludge blanket detector (Digital) | BLK - Balancing Lakes | 6 | New | 98970.0943 | Quantity |  | Number
|  | Sludge Mixers - M&E | 2G - Sludge Centre | 1 | New | 116397.0359 | Total Volume (m3) | 168 | m3
|  | Sludge Tanks, Pre-Fabricated, Circular - Civil | 2F - Sludge Handling | 1 | New | 297912.8699 | Total Volume (m3) | 168 | m3
|  | Aeration, Fine Bubble Diffusers | 2E - Secondary Treatment | 1 | New | 3373282.5302 | Total Volume (m3) | 10032 | m3
|  | Aeration Tanks, Rectangular - Civil | 2E - Secondary Treatment | 1 | New | 1778768.0975 | Total Volume (m3) | 10032 | m3
|  | Rigid Pipework <#4> | AES - Aeartion (Secondary) | 1 | New | 336391.6 | Length | 200 | m
[7 empty] | Diameter | 400 | mm
|  | Platform | SBS - Site Services | 1 | New | 51982.7399 | Area | 20 | m2
|  | Kiosk | SBS - Site Services | 1 | New | 178114.7685 | Area | 30 | m2
|  | PLC | SBS - Site Services | 1 | New | 19549.1758 | In/Out Cards | 3 | Number
|  | Cabling Ducting | SBS - Site Services | 1 | New | 69012.3619 | Length | 150 | m
|  | Landscaping <#2> | SBS - Site Services | 1 | New | 70332.2606 | Area | 750 | m2
|  | Steps | SBS - Site Services | 1 | New | 3920.4395 | Height | 1 | m
|  | Transformer | SBS - Site Services | 1 | New | 19521.4229 | Total Installed Power (inc standby) | 167 | kW
|  | Transformer Starter | SBS - Site Services | 1 | New | 28356.5439 | Total Installed Power | 167 | kW
|  | Total Asset direct costs |  |  |  | 10724013.6438
|  | Permit Cost |  |  |  | 9056
|  | Site wide Electrical Distribution |  |  |  | 617151.5
Location Factors
|  |  | Are temporary works required to keep the existing plant operational? |  |  | 785238.83
|  |  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 161136.07
|  |  | Does the site have poor ground conditions - does it need piling? |  |  | 304185.93
|  |  | Does the solution need modelling prior to delivery? |  |  | 22994.14
|  |  | Does the solution require an extensive planning effort? |  |  | 65762.45
|  |  | Does the statutory power supply need upgrading? |  |  | 380638.9
|  |  | Is an Environmental Impact Assessment (EIA) report required? |  |  | 238354.64
|  | Total Location Factor Costs (Temporary works, land purchase modelling, EIA, power upgrade,piling, ) |  |  |  | 1958310.96
|  | Total Oncost |  |  |  | 4109767.25
|  | Grand Total CAPEX |  |  |  | 17418299.3538
| Investment ID | I040871
| Investment Title | Oakham WRC OAKHST Disinfection
| Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
|  | Rigid Pipework | SWOLST-2A-PUM | 1 | New | 114638.7619 | Length | 110 | m
[7 empty] | Diameter | 300 | mm
|  | UV Disinfection civil | SWOLST-2H | 1 | New | 264742.8282 | Flow (m3/d) | 9775 | m3/d
[7 empty] | UV Dose Required | 20 | mJ/cm2
|  | UV Disinfection (M&E) | SWOLST-2H | 1 | New | 1328169.628 | Flow (m3/d) | 9775 | m3/d
[7 empty] | UV Dose Required | 20 | mJ/cm2
|  | Roads | SWOLST-SS | 1 | New | 24360.7023 | Area | 150 | m2
|  | Boundary Fencing | SWOLST-SS | 1 | New | 11715.6856 | Length | 50 | m
|  | Washwater Pressure Pipelines | SWOLST-SS | 1 | New | 7596.7251 | Length | 50 | m
|  | Landscaping | SWOLST-SS | 1 | New | 8296.5083 | Area | 100 | m2
|  | Standby Generation | SS - Site Services | 1 | New | 151321.8 | Total Installed Power | 112 | kW
|  | Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 41973.004 | Total Installed Power | 12 | kW
|  | Rigid Pipework <#2> | TUV - UV Treatment | 1 | New | 59585 | Length | 100 | m
[7 empty] | Diameter | 300 | mm
|  | Pumps, Supernatant - M&E | 2A - Catchment Pumping | 1 | New | 141716.58 | Total Installed Power | 12 | kW
|  | Biodiversity Net Gain | SS - Site Services | 1 | New | 60000 | Units | 2 | Number
|  | Telemetry | SS - Site Services | 1 | New | 13643.0426 | Quantity | 1 | Number
|  | Storm Tanks, Circular - M&E | 2C - Preliminary Treatment | 1 | New | 994744.4784 | Total Volume (m3) | 4873 | m3
|  | Storm Tanks, Circular - Civil | 2C - Preliminary Treatment | 1 | New | 361880.3179 | Total Volume (m3) | 4873 | m3
|  | Rigid Pipework <#3> | STH - Storm Handling | 1 | New | 124920.9 | Length | 50 | m
[7 empty] | Diameter | 600 | mm
|  | PLC | SBS - Site Services | 1 | New | 10167.5988 | In/Out Cards | 1 | Number
|  | Transformer | SBS - Site Services | 1 | New | 14917.0456 | Total Installed Power (inc standby) | 112 | kW
|  | Transformer Starter | SBS - Site Services | 1 | New | 24209.3212 | Total Installed Power (inc standby) | 112 | kW
|  | Cabling Ducting | SBS - Site Services | 1 | New | 88922.1413 | Length | 200 | m
|  | Kiosks | SS - Site Services | 1 | New | 124150.65 | Area | 20 | m2
|  | Platform | SBS - Site Services | 1 | New | 100132.2415 | Area | 40 | m2
|  | Steps | SBS - Site Services | 1 | New | 3920.4395 | Height | 1 | m
|  | Landscaping <#2> | SS - Site Services | 1 | New | 13395.8042 | Area | 200 | m2
|  | Total Asset direct costs |  |  |  | 4089121.2046
|  | Permit Cost |  |  |  | 9056
|  | Site wide Electrical Distribution |  |  |  | 235645.19
Location Factors
|  |  | Are temporary works required to keep the existing plant operational? |  |  | 299825.49
|  |  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 61526.12
|  |  | Does the site have poor ground conditions - does it need piling? |  |  | 116146.44
|  |  | Does the solution need modelling prior to delivery? |  |  | 8779.79
|  |  | Does the solution require an extensive planning effort? |  |  | 25109.89
|  |  | Does the statutory power supply need upgrading? |  |  | 145338.26
|  |  | Is an Environmental Impact Assessment (EIA) report required? |  |  | 91010.27
|  | Total Location Factor Costs (Temporary works, land purchase modelling, EIA, power upgrade,piling, ) |  |  |  | 747736.26
|  | Total Oncost |  |  |  | 1583004.64
|  | Grand Total CAPEX |  |  |  | 6664563.2946
|  | Investment ID | I031906
|  | Investment Title | Melton WRC MELTST Disinfection
| Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
|  | Rigid Pipework - Rising Main | SWOLST-2A-PUM | 1 | New | 114638.7619 | Length | 110 | m
[7 empty] | Diameter | 300 | mm
|  | Storm Tanks, Circular - Civil | SWOLST-2C | 1 | New | 282267.303 | Total Volume (m3) | 1766 | m3
|  | Storm Tanks, Circular M&E | SWOLST-2C | 1 | New | 431182.8049 | Total Volume (m3) | 1766 | m3
|  | UV Disinfection civil | SWOLST-2H | 1 | New | 262658.2447 | Flow | 4148 | m3/d
[7 empty] | UV Dose Required | 20 | mJ/cm2
|  | UV Disinfection (M&E) | SWOLST-2H | 1 | New | 1321000.653 | Flow | 4148 | m3/d
[7 empty] | UV Dose Required | 20 | mJ/cm2
|  | Roads | SWOLST-SS | 1 | New | 24360.7023 | Area | 150 | m2
|  | Boundary Fencing -General | SWOLST-SS | 1 | New | 11715.6856 | Length | 50 | m
|  | Washwater Pressure Pipelines | SWOLST-SS | 1 | New | 7596.7251 | Length | 50 | m
|  | Landscaping | SWOLST-SS | 1 | New | 8296.5083 | Area | 100 | m2
|  | Number of telemetry outstations | SWOLST-SS | 1 |  | 13643.0426 | Units | 1 | Number
|  | Standby Generation | SS - Site Services | 1 | New | 105027.4 | Total Installed Power | 66 | kW
|  | Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
|  | Pumps, Supernatant - M&E | 2A - Catchment Pumping | 1 | New | 124864.7565 | Total Installed Power (inc standby) | 8 | kW
|  | Rigid Pipework <#2> Interprocess | TUV - UV Treatment | 1 | New | 26811 | Length | 50 | m
[7 empty] | Diameter | 250 | mm
|  | Biodiversity Net Gain | SS - Site Services | 1 | New | 60000 | Units | 2 | units
|  | Telemetry | SS - Site Services | 1 | New | 13643.0426 | Units | 1 | Number
|  | PLC- process control | SBS - Site Services | 1 | New | 10167.5988 | Units | 1
|  | Transformer | SBS - Site Services | 1 | New | 10447.856 | Installed Power | 66 | kW
|  | Transformer Starter | SBS - Site Services | 1 | New | 19637.1116 | Installed Power | 66 | kW
|  | Steps | SBS - Site Services | 1 | New | 3920.4395 | Height | 1 | m
|  | Platform | SBS - Site Services | 1 | New | 51982.7399 | Area | 20 | m2
|  | Landscaping <#2> | SS - Site Services | 1 | New | 8296.5083 | Area | 100 | m2
|  | Kiosks - LPBC4 | SS - Site Services | 1 | New | 232078.886 | Area | 40 | m2
|  | Cabling Ducting - Up to 12 ways | SBS - Site Services | 1 | New | 48280.7032 | Length | 100 | m
|  | Total Asset direct costs |  |  |  | 3228844.5062
|  | Permit Cost |  |  |  | 9056
|  | Site wide Electrical Distribution |  |  |  | 186179.2791
Location Factors
|  |  | Are temporary works required to keep the existing plant operational? |  |  | 236887.0492
|  |  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 48610.7491
|  |  | Does the site have poor ground conditions - does it need piling? |  |  | 91765.3382
|  |  | Does the solution need modelling prior to delivery? |  |  | 6936.7619
|  |  | Does the solution require an extensive planning effort? |  |  | 19838.8978
|  |  | Does the statutory power supply need upgrading? |  |  | 114829.2997
|  | Total Location Factor Costs (Temporary works, land purchase modelling, power upgrade,piling, ) |  |  |  | 518868.0959
|  | On Cost |  |  |  | 1233613.9473
|  | Grand Total CAPEX |  |  |  | 5176561.8285
Investment ID | I040852
Investment Title | Haslingfield WRC Disinfection
Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
| Rigid Pipework | SWOLST-2A-PUM | 1 | New | 114638.7619 | Length | 110 | m
[6 empty] | Diameter | 300 | mm
| UV Disinfection civil | SWOLST-2H | 1 | New | 279167.9026 | Flow (m3/d) | 7425 | m3/d
[6 empty] | UV Dose Required | 40 | mJ/cm2
| UV Disinfection (M&E) | SWOLST-2H | 1 | New | 1626441.1405 | Flow (m3/d) | 7425 | m3/d
[6 empty] | UV Dose Required | 40 | mJ/cm2
| Roads | SWOLST-SS | 1 | New | 24360.7023 | Area | 150 | m2
| Boundary Fencing | SWOLST-SS | 1 | New | 11715.6856 | Length | 50 | m
| Washwater Pressure Pipelines | SWOLST-SS | 1 | New | 7596.7251 | Length | 50 | m
| Landscaping | SWOLST-SS | 1 | New | 8296.5083 | Area | 100 | m2
| Standby Generation | SS - Site Services | 1 | New | 201641.8 | Total Installed Power | 162 | kW
| Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power | 8 | kW
| Rigid Pipework <#2> | TUV - UV Treatment | 1 | New | 59585 | Length | 100 | m
[6 empty] | Diameter | 300 | mm
| Pumps, Supernatant - M&E | 2A - Catchment Pumping | 1 | New | 124864.7565 | Total Installed Power | 8 | kW
| Biodiversity Net Gain | SS - Site Services | 1 | New | 60000 | Units | 2 | Number
| Telemetry | SS - Site Services | 1 | New | 13643.0426 | Quantity | 1 | Number
| Storm Tanks, Circular - M&E | 2C - Preliminary Treatment | 1 | New | 743898.2696 | Total Volume (m3) | 3399 | m3
| Storm Tanks, Circular - Civil | 2C - Preliminary Treatment | 1 | New | 331336.2003 | Total Volume (m3) | 3399 | m3
| Rigid Pipework <#3> | STH - Storm Handling | 1 | New | 124920.9 | Length | 50 | m
[6 empty] | Diameter | 600 | mm
| Sludge Mixers - M&E | 2F - Sludge Handling | 1 | New | 108656.4567 | Total Volume (m3) | 140 | m3
| Sludge Tanks, Pre-Fabricated, Circular - Civil | 2F - Sludge Handling | 1 | New | 278456.2383 | Total Volume (m3) | 140 | m3
| Rigid Pipework <#4> | AES - Aeartion (Secondary) | 1 | New | 127372.8 | Length | 100 | m
[6 empty] | Diameter | 300 | mm
| Aeration, Fine Bubble Diffusers | 2E - Secondary Treatment | 1 | New | 1628705.055 | Total Volume (m3) | 3713 | m3
| Aeration Tanks, Rectangular - Civil | 2E - Secondary Treatment | 1 | New | 1161426.6092 | Total Volume (m3) | 3713 | m3
| PLC | SBS - Site Services | 1 | New | 10167.5988 | In/Out Cards | 1 | Number
| Transformer | SBS - Site Services | 1 | New | 19125.9054 | Total Installed Power (inc standby) | 162 | kW
| Transformer Starter | SBS - Site Services | 1 | New | 28017.4214 | Total Installed Power (inc standby) | 162 | kW
| Cabling Ducting | SBS - Site Services | 1 | New | 88922.1413 | Length | 200 | m
| Kiosks | SS - Site Services | 1 | New | 232078.886 | Area | 40 | m2
| Platform | SBS - Site Services | 1 | New | 100132.2415 | Area | 40 | m2
| Steps | SBS - Site Services | 1 | New | 3920.4395 | Height | 1 | m
| Landscaping <#2> | SS - Site Services | 1 | New | 8296.5083 | Area | 100 | m2
| Total Asset direct costs |  |  |  | 7563711.7291
| Permit Cost |  |  |  | 9056
| Site wide Electrical Distribution |  |  |  | 435434.1444
Location Factors
|  | Are temporary works required to keep the existing plant operational? |  |  | 554028.9451
|  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 113690.3099
|  | Does the site have poor ground conditions - does it need piling? |  |  | 214619.8102
|  | Does the solution need modelling prior to delivery? |  |  | 16223.6259
|  | Does the solution require an extensive planning effort? |  |  | 46399.006
|  | Does the statutory power supply need upgrading? |  |  | 268561.5613
|  | Is an Environmental Impact Assessment (EIA) report required? |  |  | 168172.2393
| Total Location Factor Costs |  |  |  | 1381695.4976
| Total Oncost |  |  |  | 2899665.5964
| Grand Total |  |  |  | 12289562.9676
Investment ID | I031762
Investment Title | Southwold WRC Disinfection
Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
| Rigid Pipework <#3> | SWOLST-2A-PUM | 1 | New | 52108.4941 | Length | 55 | m
[6 empty] | Diameter | 250 | mm
| Rigid Pipework | SWOLST-2A-PUM | 1 | New | 114638.7619 | Length | 110 | m
[6 empty] | Diameter | 300 | mm
| Pumping Stations, Interprocess Civils | SWOLST-2A | 1 | New | 50414.7457 | Total Installed Power (inc standby) | 22 | kW
| Storm Tanks, Circular - Civil | SWOLST-2C | 3 | New | 736751.828 | Total Volume (m3) | 1000 | m3
| Storm Tanks, Circular M&E | SWOLST-2C | 3 | New | 803880.339 | Total Volume (m3) | 1000 | m3
| Primary Tanks Desludging and Scrapers, Circular (M&E) | SWOLST-2D | 1 | New | 278251.2007 | Total Volume (m3) | 190 | m3
| Humus Tanks Desludging and Scrapers, Circular | SWOLST-2E | 1 | New | 253262.2037 | Total Volume (m3) | 160 | m3
| Humus Tanks, Cirular (civil) | SWOLST-2E | 1 | New | 515115.177 | Total Volume (m3) | 160 | m3
| UV Disinfection civil | SWOLST-2H | 1 | New | 262658.2447 | Flow (m3/d) | 5940 | m3/d
[6 empty] | UV Dose Required | 20 | mJ/cm2
| UV Disinfection (M&E) | SWOLST-2H | 1 | New | 1321000.653 | Flow (m3/d) | 5940 | m3/d
[6 empty] | UV Dose Required | 20 | mJ/cm2
| Roads | SWOLST-SS | 1 | New | 24360.7023 | Area | 150 | m2
| Boundary Fencing | SWOLST-SS | 1 | New | 11715.6856 | Length | 50 | m
| Washwater Pressure Pipelines | SWOLST-SS | 1 | New | 7596.7251 | Length | 50 | m
| Landscaping | SWOLST-SS | 1 | New | 8296.5083 | Area | 150 | m2
| Number of telemetry outstations | SWOLST-SS | 1 | New | 13643.0426 | Quantity | 1 | Number
| Standby Generation | SS - Site Services | 1 | New | 147296.2 | Total Installed Power | 108 | kW
| Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
| Rigid Pipework <#2> | TUV - UV Treatment | 1 | New | 53480.65 | Length | 50 | m
[6 empty] | Diameter | 250 | mm
| Pumps, Supernatant - M&E <#2> | 2A - Catchment Pumping | 1 | New | 171242.7849 | Total Installed Power (inc standby) | 22 | kW
| Pumps, Storm - M&E | 2A - Catchment Pumping | 1 | New | 129164.8379 | Total Installed Power (inc standby) | 8 | kW
| Biodiversity Net Gain | SS - Site Services | 1 | New | 60000 | Units | 2 | Number
| Sludge blanket detector (Digital) | STH - Storm Handling | 4 | New | 65980.0629 | Quantity | 1 | Number
| Sludge Mixers - M&E | 2F - Sludge Handling | 1 | New | 99182.7533 | Total Volume (m3) | 112 | m3
| Sludge Tanks, Pre-Fabricated, Circular - Civil | 2F - Sludge Handling | 1 | New | 258999.6067 | Total Volume (m3) | 112 | m3
| PLC | SBS - Site Services | 1 | New | 10167.5988 | In/Out Cards | 1 | Number
| Transformer Starter | ELE - Electrical Distribution | 1 | New | 23863.3407 | Total Installed Power | 108 | kW
| Transformer | ELE - Electrical Distribution | 1 | New | 14556.1805 | Total Installed Power | 108 | kW
| Platform | BLD - BUILDING | 1 | New | 26986.3653 | Area | 10 | m2
| Steps | BLD - BUILDING | 1 | New | 3920.4395 | Height | 1 | m
| Cabling Ducting | SBS - Site Services | 1 | New | 92828.155 | Length | 210 | m
| Landscaping <#2> | SS - Site Services | 1 | New | 43795.332 | Area | 1110 | m2
| Kiosks | SS - Site Services | 1 | New | 70186.5336 | Area | 10 | m2
| Primary Tanks, Circular - Civil | 2D - Primary Treatment | 1 | New | 284505.2811 | Volume | 190 | m3
| External Site Lighting | SBS - Site Services | 3 | New | 13772.8275 | Depth | 150 | m
| Rigid Pipework <#4> | SBS - Site Services | 1 | New | 118440.2054 | Length | 200 | m
[6 empty] | Diameter | 250 | mm
| Rigid Pipework <#5> | TER - Tertiary Filtration | 1 | New | 106961.3 | Length | 100 | m
[6 empty] | Diameter | 300 | mm
| Rigid Pipework <#6> | STH - Storm Handling | 1 | New | 127372.8 | Length | 100 | m
[6 empty] | Diameter | 250 | mm
| Rigid Pipework <#7> | FSM - Final Settlement | 1 | New | 53480.65 | Length | 50 | m
[6 empty] | Diameter | 250 | mm
| Rigid Pipework <#8> | BIO - Biological Filtration - ST | 1 | New | 53480.65 | Length | 50 | m
[6 empty] | Diameter | 250 | mm
| Rigid Pipework <#9> | PSM - Primary Settlement | 1 | New | 53480.65 | Length | 50 | m
[6 empty] | Diameter | 250 | mm
| Aeration, Fine Bubble Diffusers | 2E - Secondary Treatment | 1 | New | 2243545.0672 | Total Volume (m3) | 5940 | m3
| Aeration Tanks, Rectangular - Civil | 2E - Secondary Treatment | 1 | New | 1420717.8257 | Total Volume (m3) | 5940 | m3
| Total Asset direct costs |  |  |  | 10237428.4421
| Permit Cost |  |  |  | 9056
| Site wide Electrical Distribution |  |  |  | 589172.8554
Location Factors
|  | Are temporary works required to keep the existing plant operational? |  |  | 749639.9163
|  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 153830.9417
|  | Does the site have a high water table - does it need dewatering? |  |  | 216508.91
|  | Does the site have poor ground conditions - does it need piling? |  |  | 290395.6156
|  | Does the solution need modelling prior to delivery? |  |  | 21951.7006
|  | Does the solution require an extensive planning effort? |  |  | 62781.1007
|  | Does the statutory power supply need upgrading? |  |  | 363382.5779
|  | Is an Environmental Impact Assessment (EIA) report required? |  |  | 227548.8032
|  | Is an archaeological study required? |  |  | 36601.7867
|  | Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 273723.615
|  | Is the site of Special Scientific interest? |  |  | 36745.4562
| Total Location Factor Costs |  |  |  | 2433110.424
| Total Oncost |  |  |  | 4097487.7305
| Grand Total |  |  |  | 17366255.452
Investment ID | I031837
Investment Title | Tollesbury WRC TOLLST Disinfection
Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
| UV Disinfection - M&E | 2H - Tertiary Treatment | 1 | New | 1321000.653 | Flow (m3/d) | 1980 | m3/d
[6 empty] | UV Dose Required | 40 | mJ/cm2
| UV Disinfection - Civil | 2H - Tertiary Treatment | 1 | New | 262658.2447 | Flow (m3/d) | 1980 | m3/d
[6 empty] | UV Dose Required | 40 | mJ/cm2
| Storm Tanks, Circular - M&E | 2C - Preliminary Treatment | 1 | New | 178274.9352 | Total Volume (m3) | 473 | m3
| Storm Tanks, Circular - Civil | 2C - Preliminary Treatment | 1 | New | 204460.5624 | Total Volume (m3) | 473 | m3
| Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 3217.827 | Length | 10 | m
[6 empty] | Diameter | 75 | mm
| Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 2 | New | 72652.0647 | Total Installed Power (inc standby) | 8 | kW
| Rigid Pipework <#2> | PUM - Inter-Process Pumping | 1 | New | 13639.5326 | Length | 20 | m
[6 empty] | Diameter | 150 | mm
| Standby Generation | SS - Site Services | 1 | New | 104021 | Total Installed Power (inc standby) | 65 | kW
| Pumps, Supernatant - M&E | 2A - Catchment Pumping | 1 | New | 124864.7565 | Total Installed Power (inc standby) | 8 | kW
| Rigid Pipework <#3> | TUV - UV Treatment | 1 | New | 29792.5 | Length | 50 | m
[6 empty] | Diameter | 300 | mm
| Biodiversity Net Gain | SS - Site Services | 1 | New | 60000 | Units | 2 | Number
| Telemetry | SS - Site Services | 1 | New | 13643.0426 | Quantity | 1 | Number
| Landscaping | SS - Site Services | 1 | New | 8296.5083 | Area | 100 | m2
| Pumps, Storm - M&E | 2A - Catchment Pumping | 1 | New | 129164.8379 | Total Installed Power (inc standby) | 8 | kW
| Continuous Sand Filtration | 2H - Tertiary Treatment | 1 | New | 975327.8716 | Flow (m3/d) | 1980 | m3/d
| Sludge blanket detector (Digital) | STH - Storm Handling | 2 | New | 32990.0314 | Quantity | 1 | Number
| Sludge Mixers - M&E | 2F - Sludge Handling | 1 | New | 101756.6107 | Total Volume (m3) | 119 | m3
| Sludge Tanks, Pre-Fabricated, Circular - Civil | 2F - Sludge Handling | 1 | New | 263863.7646 | Total Volume (m3) | 119 | m3
| Rigid Pipework <#4> | AES - Aeartion (Secondary) | 1 | New | 106961.3 | Length | 100 | m
[6 empty] | Diameter | 250 | mm
| Collection Storage - Offline | 2B - Network Balancing | 1 | New | 469561.578 | Storage Volume | 220 | m3
[6 empty] | Fencing length | 50 | m
[6 empty] | Landscaping Area | 50 | m
[6 empty] | Road Length | 10 | m
[6 empty] | Telemetry | 1 | number
| Sewer - Rising Main | 03 - AW Water Recycling Infra | 1 | New | 138288.2934 | Diameter | 150 | mm
[6 empty] | Length in 3/4 Reinstatment | 310 | m
[6 empty] | Depth | 1.5 | m
| Sewer - Gravity | 03 - AW Water Recycling Infra | 1 | New | 556669.5584 | Diameter | 250 | mm
[6 empty] | Length in 3/4 Reinstatment | 310 | m
[6 empty] | Depth | 5 | m
[6 empty] | Manholes | 6 | Number
| Rigid Pipework <#5> | AES - Aeartion (Secondary) | 1 | New | 86549.8 | Length | 100 | m
[6 empty] | Diameter | 200 | mm
| Aeration, Fine Bubble Diffusers | 2E - Secondary Treatment | 1 | New | 1150250.7482 | Total Volume (m3) | 1980 | m3
| Aeration Tanks, Rectangular - Civil | 2E - Secondary Treatment | 1 | New | 886919.8195 | Total Volume (m3) | 1980 | m3
| Steps | SBS - Site Services | 1 | New | 3920.4395 | Height | 1 | m
| Platform | SBS - Site Services | 1 | New | 51982.7399 | Area | 20 | m2
| Transformer Starter | ELE - Electrical Distribution | 1 | New | 19518.805 | Installed Power | 65 | kW
| Transformer | ELE - Electrical Distribution | 1 | New | 10340.9954 | Installed Power | 65 | kW
| PLC | SBS - Site Services | 1 | New | 10167.5988 | In/Out cards | 1 | Number
| Cabling Ducting | SBS - Site Services | 1 | New | 92828.155 | Length | 210 | m
| Kiosks | SS - Site Services | 1 | New | 124150.6511 | Area | 20 | m2
| Landscaping <#2> | SS - Site Services | 1 | New | 4403.8978 | Area | 40 | m2
| Total Asset direct costs |  |  |  | 7612139.1233
| Permit Cost |  |  |  | 9056
| Site wide Electrical Distribution |  |  |  | 438218.7196
Location Factors
|  | Are temporary works required to keep the existing plant operational? |  |  | 557571.9269
|  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 114417.3526
|  | Does the solution need modelling prior to delivery? |  |  | 16327.375
|  | Does the solution require an extensive planning effort? |  |  | 46695.7249
|  | Does the statutory power supply need upgrading? |  |  | 270278.9963
|  | Is an Environmental Impact Assessment (EIA) report required? |  |  | 169247.6907
| Total Location Factor Costs |  |  |  | 1174539.0662
| Total Oncost |  |  |  | 2851508.8623
| Grand Total |  |  |  | 12085461.7714
Investment ID | I031776
Investment Title | Easton WRC ESTNST Disinfection
Direct cost | Name | Functional Location | Quantity | Source | Capital Cost | Attribute | Value | Unit of measure
| Storm Tanks, Circular - M&E | 2C - Preliminary Treatment | 1 | New | 109862.33 | Total Volume (m3) | 71 | m3
| Storm Tanks, Circular - Civil | 2C - Preliminary Treatment | 1 | New | 128528.8576 | Total Volume (m3) | 71 | m3
| Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 3217.827 | Length | 10 | m
[6 empty] | Diameter | 75 | mm
| Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 2 | New | 26672.4706 | Total Installed Power (inc standby) | 4 | kW
| Standby Generation | SS - Site Services | 1 | New | 63765 | Total Installed Power (inc standby) | 25 | kW
| Biodiversity Net Gain | SS - Site Services | 1 | New | 4500 | Units | 0.15 | Number
| Telemetry | SS - Site Services | 1 | New | 13643.04 | Quantity | 1 | Number
| Landscaping | SS - Site Services | 1 | New | 8296.5083 | Area | 100 | m2
| Road | SS - Site Services | 1 | New | 17174.8997 | Area | 100 | m2
| Pumps, Storm - M&E | 2A - Catchment Pumping | 1 | New | 95529.1798 | Total Installed Power (inc standby) | 4 | kW
| Pumping Station Civil | 03 - AW Water Recycling Infra | 1 | New | 72129.5814 | Volume | 5 | m3
| Pumping Station MEICA | 03 - AW Water Recycling Infra | 1 | New | 67438.7255 | Total Installed Power (inc standby) | 6 | kW
| Sewer - Rising Main | 03 - AW Water Recycling Infra | 1 | New | 1399518.881 | Diameter | 75 | mm
[6 empty] | Length in Field | 7500 | m
[6 empty] | Length in Verge | 200 | m
[6 empty] | Length in Directional Drill | 200 | m
[6 empty] | Length in Type 3/4 | 100 | m
[6 empty] | Depth | 2 | m
| Total Asset direct costs |  |  |  | 2010277.3009
| Permit Cost |  |  |  | 9056
| Site wide Electrical Distribution |  |  |  | 116111.67
Location Factors
|  | Are temporary works required to keep the existing plant operational? |  |  | 147735.83
|  | Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 30316.34
|  | Does the solution need modelling prior to delivery? |  |  | 4326.15
|  | Does the solution require an extensive planning effort? |  |  | 12372.63
|  | Does the statutory power supply need upgrading? |  |  | 71613.88
|  | Is an Environmental Impact Assessment (EIA) report required? |  |  | 44844.34
| Total Location Factor Costs |  |  |  | 311209.17
| Additional 20% overhead for modelling |  |  |  | 643672
| Total Oncost |  |  |  | 771709.85
| Grand Total |  |  |  | 3862035.9909

## Microbiological CBA
the cost show are total costs including Labour, Plant, materials and prelims, Location factors and On costs
C55 ID | Investment Name | Alternative Description | Description | Option Selected | AMP8 Capex (£m) | AMP8 OPEX (£m) | Anualised OPEX (£m) | WLC (£m) | EAB (£m) | EAC (£m) | EAV (£m) | Mitigated Risk (£m) | Risk Index (value)
I031906 | Melton WRC MELTST Disinfection | DD Melton WRC UV for FFT Flows & Storm Tank (UV Updated) | Improvements - UV plant (for Final Effluent). but need to separate and settle the excess Storm flows. UV Model updated July 2024 with advice from Trojan. Melton is currently an ALL flows works DWF = 1,257 m3/d, Estimated FFT would be 3,483 m3/d. Full Formula A flow is circa 7,967 m3/d. Estimated Max flow c 17,600 m3/d. Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system | Yes | 5.1766 | 0.66851 | 0.2057 | 9.3748 | 7.0152 | 0.49109 | 6.5241 | 8.2098 | 1.1419
I040852 | Haslingfield WRC HASLST Disinfection | DD Haslingfield WRC ASP & UV for FFT & Storm Storage | Improvements - ASP & UV plant on Final Effluent for FFT flows 6750 m3/d). DWF =2,250 m3/d. Haslingfield WRC = c10,000 PE, Lift pumping station required to lift the treated full flow to treatment flows to the new UV Plant.. Part flow Aeration tank, Retiary Solids Removal and UV plant. Storm Tanks estimated to reduce spills to 2 per annum. Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | Yes | 12.2896 | 0.15339 | 0.43586 | 18.9121 | 5.8294 | 0.9907 | 4.8387 | 8.1043 | 2.3336
|  | DD Haslingfield WRC MBR & UV for FFT & Storm Storage | Improvements - MBR & UV plant on Final Effluent for FFT flows 6750 m3/d). DWF =2,250 m3/d. Haslingfield WRC = c10,000 PE, Lift pumping station required to lift the treated full flow to treatment flows to the new UV Plant.. Part flow Aeration tank, Retiary Solids Removal and UV plant. Storm Tanks estimated to reduce spills to 2 per annum. Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | No | 13.686 | 0 | 0.61779 | 23.2144 | 5.8271 | 1.2161 | 4.611 | 8.1011 | 2.8656
|  | DD Haslingfield WRC Storm Storage and Pump Away ROUGH ESTIMATE DO NOT USE | Improvements - UV plant on Final Effluent for FFT flows 5850 m3/d). DWF =2,250 m3/d. Haslingfield WRC = c10,000 PE, Storm Tanks estimated to reduce spills to 2 per annum. Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system THIS OPTION IS HIGHLY UNLIKELY TO BE ACCEPTABLE TO THE EA, IT ONLY MOVES THE PROBLEM THE PUMP AWAY SIZES ARE ESTIMATES WHICH WOULD NEED TO BE VALIDATED BY CATCHMENT MODELLING UNAVAILABLE AT THE POINT. THE POTENTIAL COSTING ERROR WILL BE SIGNIFICANT. DUE TO TIME LIMITATIONS LAND TYPES & DIRECTIONAL DRILLING ESTMATED AS NOMINAL VALUES. | No | 20.3397 | 0 | 0.34386 | 22.8218 | 5.8869 | 1.1955 | 4.6914 | 8.1842 | 2.7885
I040818 | Manningtree WRC MANNST Disinfection | DD Manningtree WRC ASP & UV for FFT & Storm Storage | Improvements - UV plant on Final Effluent for FFT flows (9,000 m3/d). DWF =2,999 m3/d. Manningtree WRC = c12,000 PE, but designed for 17,000 PE. Hemmed in by Railway Lines. Lift pumping station required to lift the treated full flow to treatment flows to the new UV Plant.. Install ASP, and UV plant. Design for 17,000 = 10,032 m3/d. Storm Tanks estimated to reduce spills to 2 per annum. Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | Yes | 17.4183 | 0.19294 | 0.55713 | 26.4404 | 5.807 | 1.3851 | 4.4219 | 8.0731 | 3.2751
|  | DD Manningtree WRC TSR & UV for FFT & Storm Storage | Improvements - UV plant & TSR on Final Effluent for FFT flows (9,000 m3/d). DWF =2,999 m3/d. Manningtree WRC = c12,000 PE, but designed for 17,000 PE. Hemmed in by Railway Lines. Lift pumping station required to lift the treated full flow to treatment flows to the new UV Plant.. Install MBR and UV plant. Design for 17,000 = 10,032 m3/d. Storm Tanks estimated to reduce spills to 2 per annum. Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | No | 14.2412 | 0 | 0.49003 | 21.8174 | 5.8278 | 1.1429 | 4.6849 | 8.1021 | 2.6928
|  | DD Manningtree WRC Storm Storage and Pump Away - ROUGH ESTIMATE DO NOT USE | Improvements - UV plant on Final Effluent for FFT flows (7,344 m3/d). DWF =2,999 m3/d. Manningtree WRC = c10,000 PE, but designed for 17,000 PE. Hemmed in by Railway Lines. Storm Tanks estimated to reduce spills to 2 per annum. Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system Pump Away to Coast Est 20km away via 3 Pumping Stations THIS OPTION IS HIGHLY UNLIKELY TO BE ACCEPTABLE TO THE EA, IT ONLY MOVES THE PROBLEM THE PUMP AWAY SIZES ARE ESTIMATES WHICH WOULD NEED TO BE VALIDATED BY CATCHMENT MODELLING UNAVAILABLE AT THE POINT. THE POTENTIAL COSTING ERROR WILL BE SIGNIFICANT. DUE TO TIME LIMITATIONS LAND TYPES & DIRECTIONAL DRILLING ESTMATED AS NOMINAL VALUES. | No | 30.2197 | 0 | 0.75157 | 36.8507 | 5.8869 | 1.9304 | 3.9565 | 8.1842 | 4.5027
I040840 | Sudbury WRC SUDBST Disinfection | DD Sudbury WRC ASP & UV for FFT + Storm Storage | Improvements - Activated Sludge Plant. & UV Plant for FFT Flows (Final Effluent). Excess Storm Flows are estimated at (48,174 - 9,677) = 38,497 m3/d. Storm Tanks to settle storm flows and reduce spills. Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. Offline Storm Storage at Sudbury Bailey & Coates Cross Street CSO, Sudbury The Croft CSO and Sudbury Conard RD SP. Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system | Yes | 24.0851 | 0.2306 | 0.73912 | 35.1201 | 5.7776 | 1.8397 | 3.9379 | 8.0323 | 4.3724
|  | DD Sudbury WRC Storm Storage & Pump Away ROUGH ESTIMATE DO NOT USE | Excess Storm Flows are estimated at (48,174 - 9,677) = 38,497 m3/d. Storm Tanks to settle storm flows and reduce spills. Offline Storm Storage at Sudbury Bailey & Coates Cross Street CSO, Sudbury The Croft CSO and Sudbury Conard RD SP. Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system Pump Away of FFT and Storm Flows to Downstream of the Bathing water area Estimated 1.8-2.0km THIS OPTION IS HIGHLY UNLIKELY TO BE ACCEPTABLE TO THE EA, IT ONLY MOVES THE PROBLEM THE PUMP AWAY SIZES ARE ESTIMATES WHICH WOULD NEED TO BE VALIDATED BY CATCHMENT MODELLING UNAVAILABLE AT THE POINT. THE POTENTIAL COSTING ERROR WILL BE SIGNIFICANT. | No | 15.1566 | 0 | 0.22153 | 17.1702 | 5.9141 | 0.89945 | 5.0146 | 8.101 | 2.1195
|  | DD Sudbury WRC MBR & UV for FFT + Storm Storage | Improvements - UV Plant for Storm disinfection and UV Plant for FFT Flows (Final Effluent). MBR . DWF = 3,441 m3/d. FFT = 11,356 m3/d. Excess Storm Flows are estimated at (48,174 - 9,677) = 38,497 m3/d. Storm Tanks to settle storm flows and reduce spills. Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. Offline Storm Storage at Sudbury Bailey & Coates Cross Street CSO, Sudbury The Croft CSO and Sudbury Conard RD SP. Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system | No | 19.8971 | 0 | 1.0489 | 34.7009 | 5.7985 | 1.8178 | 3.9807 | 8.0613 | 4.3046
I031905 | Woodbridge WRC WOODST Disinfection | DD Woodbridge WRC ASP &UV for FFT + Storm Tanks | Improvements - ASP & UV Plant for FFT Flows (Final Effluent) and Storm Tanks to manage Storm flows. FFT Flows are 15,840 m3/d. (3 .3times cDWF) Excess Storm Flows 233 l/s are (20,130 - 8,880) = 11,250 m3/d. Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | Yes | 23.071 | 0.80577 | 0.68671 | 36.0857 | 6.1144 | 1.8903 | 4.2241 | 8.0155 | 4.502
|  | DD Woodbridge WRC TSR & UV for FFT + Storm Tanks & Power Supply | Improvements - Tertiary Solids Removal & UV Plant for FFT Flows (Final Effluent) and Storm Tanks to manage Storm flows. FFT Flows are 15,840 m3/d. (3 .3times cDWF) Excess Storm Flows 233 l/s are (20,130 - 8,880) = 11,250 m3/d. Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | No | 16.1157 | 0 | 0.56795 | 26.4865 | 6.2202 | 1.3875 | 4.8327 | 8.1541 | 3.2482
I031886 | Boston WRC Disinfection | DD Boston WRC UV & TSR Plant + Add storm storage | Improvements - ASP, Tertiary Solids Removal and UV plant Final Effluent FFT Flows. Storm storage which consists of 1 No Circular Tanks with scrapers and a Storm Return Pumping Station, 150 m2 of road and another Telemetry outstation. The existing Storm Storage is located at the TPS. Pumping Station required to lift flows through the proposed UV Plant. Pumping Station required to lift flows through the proposed Storm storage. Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. UV is the only accepted treatment by the Environment Agency for disinfection. This investment also needs to deliver ENVACTIMP4 | Yes | 24.6145 | 2.2528 | 1.001 | 43.4976 | 48.764 | 2.2786 | 46.4854 | 60.3674 | 0.72055
I031443 | King's Lynn STC Disinfection | DD Kings Lynn STC ASP & UV Plant + Liquor Treatment | Disinfection of discharge at Kings Lynn STC (PE = c95,000) - to protect the Shellfish in The Wash. 1) Provide UV treatment for the Full Flow to Treatment flows and (Sludge Liquor Treatment This includes for lifting of flows to the new UV Disinfection Plant. The additional scope of this alternative is to provide 2) Additional Storm Storage at Nar Lane No 1 PS - wet volume required = 1,382 m3. Full Volume = 1,660 m3. Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. 3) Upgraded ASP Plant and Final Tanks to manage the pin floc solids created by an exiting low sludge age. 4) Tertiary sludge liquor Treatment - mimicked by Sand Filter installation for C55 purposes. UV is the only accepted treatment by the Environment Agency for disinfection. | Yes | 57.9023 | 5.3626 | 1.7282 | 93.8901 | 19.7732 | 4.9184 | 14.8548 | 23.1416 | 4.0572
I031837 | Tollesbury WRC Disinfection | DD Tollesbury WRC ASP & TSR & UV Plant for FFT, storm storage | Provide Tertiary Solids Removal ASP and UV Disinfection Plant for Final Effluent FFT Flows. Install Blind Storm storage (Circular Tank with scraper( and a Storm Return Pumping Station. Provide a new Telemetry outstation. Provide CSO Storm Storage at Tollesbury Woodrolfe Road CSO to reduce spills . Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | Yes | 12.0855 | 0.053203 | 0.3085 | 16.4834 | 4.9433 | 0.86347 | 4.0799 | 7.0455 | 2.3396
|  | DD Tollesbury WRC MBR & UV Plant + Storm storage | Provide MBR, fine screening and UV Disinfection Plant for Final Effluent FFT Flows. Install Blind Storm storage (Circular Tank with scraper( and a Storm Return Pumping Station. Provide a new Telemetry outstation. Provide CSO Storm Storage at Tollesbury Woodrolfe Road CSO to reduce spills . Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | No | 12.0234 | 0 | 0.37424 | 17.4462 | 4.9447 | 0.91391 | 4.0308 | 7.0474 | 2.4755
I040871 | Oakham WRC OAKHST Disinfection | DD Oakham WRC ASP, UV for FFT & Storm Tanks & Power Supply | Improvements - UV plant on Final Effluent for FFT flows (8,899 m3/d). DWF = 2,962 m3/d. Oakham WRC = c13,500 PE. Lift pumping station required to lift the treated full flow to treatment flows to the new UV Plant.. ASP,, Tertiary Solids Removal and UV plant Storm Tanks estimated to reduce spills to 2 per annum. See SEW-11617 presentation stated 103 l/s for FFT = 8899 m3/d Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | No | 16.0105 | 0 | 0.38449 | 22.4479 | 5.7667 | 1.1759 | 4.5908 | 8.0971 | 2.7723
|  | DD Oakham WRC UV & MBR for FFT & Storm Tanks & Power Supply | Improvements - UV plant on Final Effluent for FFT flows (8,899 m3/d). DWF = 2,962 m3/d. Oakham WRC = c13,500 PE. Lift pumping station required to lift the treated full flow to treatment flows to the new UV Plant.. ASP,, Tertiary Solids Removal and UV plant Storm Tanks estimated to reduce spills to 2 per annum. See SEW-11617 presentation stated 103 l/s for FFT = 8899 m3/d Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | No | 14.2388 | 0 | 0.57971 | 23.2513 | 5.7768 | 1.218 | 4.5588 | 8.1112 | 2.8666
|  | DD Oakham WRC Storm Storage and Pumps Away - ROUGH ESTIMATE DO NOT USE | Improvements - UV plant on Final Effluent for FFT flows (8,899 m3/d). DWF = 2,962 m3/d. Oakham WRC = c13,500 PE. Storm Tanks estimated to reduce spills to 2 per annum. See SEW-11617 presentation stated 103 l/s for FFT = 8899 m3/d Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system Pump Away back to the Welland or Nene near Stamford or Wansford respectively (Post Rutland Intakes) up to 24km (3 No Interstage Pumping Stations each pumping circa 8km) THIS OPTION IS HIGHLY UNLIKELY TO BE ACCEPTABLE TO THE EA, IT ONLY MOVES THE PROBLEM THE PUMP AWAY SIZES ARE ESTIMATES WHICH WOULD NEED TO BE VALIDATED BY CATCHMENT MODELLING UNAVAILABLE AT THE POINT. THE POTENTIAL COSTING ERROR WILL BE SIGNIFICANT. DUE TO TIME LIMITATIONS LAND TYPES & DIRECTIONAL DRILLING ESTMATED AS NOMINAL VALUES. | No | 31.2138 | 0 | 0.75113 | 37.4278 | 5.8044 | 1.9606 | 3.8437 | 8.15 | 4.5924
|  | DD Oakham WRC UV for FFT & Storm Tanks (Updated UV) | Improvements - UV plant on Final Effluent for FFT flows (8,899 m3/d). DWF = 2,962 m3/d. UV Model updated July 2024 with advice from Trojan. Oakham WRC = c13,500 PE. Lift pumping station required to lift the treated full flow to treatment flows to the new UV Plant.. UV plant (Civil and M&E) for 8,899 m3/d of flow. (103 l/s) Storm Tanks estimated to reduce spills to 2 per annum. See SEW-11617 presentation stated 103 l/s for FFT = 8899 m3/d Assumptions: Storm tanks at the WRC are gravitated feed from an elevated Inlet works and the return will be managed by reusing existing PS system | Yes | 6.6646 | 0.076596 | 0.24331 | 10.5134 | 5.7963 | 0.55074 | 5.2456 | 8.1386 | 1.2918
I031762 | Southwold WRC Disinfection | DD Southwold WRC ASP & UV for F.E. + storm storage | Improvements - UV disinfection plant for Final Effluent (FE). Install ASP, upgrade primary and secondary treatment to treat to the standard needed for UV treatment to be effective. Install UV treatment on Final Effluent channel. Storm storage which consists of 3 No 1,000 m3 Circular Tanks with scrapers and a Storm Return Pumping Station, 150 m2 of road and another Telemetry outstation. Storm Screen. | Yes | 17.3663 | 0.43466 | 0.42047 | 24.8951 | 4.37 | 1.3041 | 3.0659 | 5.7283 | 4.346
|  | DD Southwold WRC MBR & UV for F.E. + storm storage | Improvements - UV disinfection plant for Final Effluent (FE). Install MBR, upgrade primary and secondary treatment to treat to the standard needed for UV treatment to be effective. Install UV treatment on Final Effluent channel. Storm storage which consists of 3 No 1,000 m3 Circular Tanks with scrapers and a Storm Return Pumping Station, 150 m2 of road and another Telemetry outstation. Storm Screen. | No | 15.4444 | 0 | 0.53016 | 24.6857 | 4.3774 | 1.2931 | 3.0842 | 5.738 | 4.3022
I031776 | Easton WRC ESTNST Disinfection | DD Easton WRC UV for FFT Flows and Storm Tank & Power & Tertiary Solids | Improvements - UV plant (for FE). Install an ASP, Tertiary Solids removal & UV treatment plant on FE channel. to treat FFT Flows. Install an Inlet Works with mechanical screens to deal with the max instantaneous flows. Install full new treatment including PST, Aeration and MBR. Install Blind Storm storage (Circular Tank with scraper( and a Storm Return Pumping Station. Provide a new Telemetry outstation. Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. | No | 7.1611 | 0 | 0.24835 | 11.3082 | 6.2772 | 0.59237 | 5.6848 | 8.2289 | 1.3742
|  | DD Easton WRC Storm Storage & Pump to Framlingham WRC | Install Blind Storm storage (Circular Tank with scraper( and a Storm Return Pumping Station. Provide a new Telemetry outstation. Pump Away of FFT and Storm Flows to Framlingham WRC THIS OPTION IS HIGHLY UNLIKELY TO BE ACCEPTABLE TO THE EA (Framlingham WRC is 3 of 5 years flow non compliant now so would need major upgrade to take additional flow), DO NOT USE THE PUMP AWAY SIZES ARE ESTIMATES WHICH WOULD NEED TO BE VALIDATED BY CATCHMENT MODELLING UNAVAILABLE AT THE POINT. THE POTENTIAL COSTING ERROR WILL BE SIGNIFICANT. | Yes | 3.862 | 0.025852 | 0.021529 | 3.9321 | 6.3689 | 0.20598 | 6.163 | 8.2292 | 0.47782
I033697 | Maldon WRC MALDST Disinfection | DD Maldon WRC ASP & UV Plant for FFT & Storm Storage | Provide ASP & Tertiary Solids removal and a UV treatment plant on FE channel. to treat FFT Flows. Install Blind Storm storage (Circular Tank with scraper( and a Storm Return Pumping Station. Provide a new Telemetry outstation. Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. UV is the only accepted treatment by the Environment Agency for disinfection. | Yes | 32.819 | 1.0439 | 0.93204 | 49.5496 | 5.2131 | 2.5956 | 2.6175 | 6.8337 | 7.2507
|  | DD Maldon WRC MBR & UV Plant with Fine Screens & Storm Storage | Provide Membrane Bioreactor (MBR) and Fine Screens etc.. & UV Plant. Install Blind Storm storage (Circular Tank with scraper) and a Storm Return Pumping Station. Provide a new Telemetry outstation. Power upgrade required for high intensity UV Plant - which will run 24/7 for 365 days of the year. UV is the only accepted treatment by the Environment Agency for disinfection. | No | 29.6029 | 0 | 1.3109 | 52.1064 | 5.2325 | 2.7296 | 2.503 | 6.8592 | 7.5965
Definitions
1) Whole Life Cost - WLC (discounted) = CAPEX+CAPEX repeat+OPEX+OPEX repeat at 30 years then discounted
2) EAB – Equivalent Annualised Benefit = The benefit in £ that is expected each year following completion of the scheme
3) EAV – Equivalent Annualised Value
4) EAC - Equivalent annual cost (EAC) = the annual cost of owning, operating, and maintaining an asset over a defined period of time, in this case 30 years as per the requirements from Ofwat
5) Risk Index = Whole Life Cost/(Baseline Risk Value – Residual Risk Value)
Note on C9: Inland
Note on C12: Inland
Note on C15: Inland

## Supply side improvements
Investment Code | I043766
Investment Title | NAY4 Aylsham WW Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Quantity | 1 | each
Electrical Actuator | DWW - Dirty Wash Water Handling | 6 | New | 41449.3595 | Valve Size | 200 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 6 | New | 7510.2375 | Nominal Bore | 200 | mm
[5 empty] | Installation Complexity | non-Complex
Closed Rectangular Tank (Sloped Floor) | DWW - Dirty Wash Water Handling | 2 | New | 306398.5068 | Volume | 100 | m3
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 99829.6 | Diameter | 200 | mm
[5 empty] | Length | 130 | m
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 2 | New | 25419 | Diameter | 200 | mm
[5 empty] | Length | 3 | m
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | unit
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Ultrasonic Level | DWW - Dirty Wash Water Handling | 2 | New | 4789.8121 | Quantity | 2 | each
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 2 | New | 1832.8359 | Nominal Bore | 150 | mm
[5 empty] | Installation Complexity | Complex
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 18260.1 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 2 | number
| Total Asset direct costs |  |  | 578564.8293
Location Factors
| Site wide Electrical Distribution |  |  | 33267.48 | Power to new assets
| Are specialist scaffolding resources required to access assets? |  |  | 23702.46 | required for access to install asset
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 17745.87 | Digging out of bank for extra site space
| Total Location Factor Costs |  |  | 74715.81
| On Cost |  |  | 291212.81
| Grand Total |  |  | 944493.4493
Investment Code | I043776
Investment Title | SUT6 Barnham Cross WW Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty | 1 | each
Electrical Actuator | DWW - Dirty Wash Water Handling | 2 | New | 12349.2896 | Valve Size | 150 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 6 | New | 7510.2375 | Nominal Bore | 200 | mm
Tank Cover <#2> | RWS - Raw Water Storage | 1 | New | 74334.388 | Purpose of Covers | Preventing External Contamination
[5 empty] | Cover Plan Area | 100 | m2
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 18260.1 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 2 | Replacement | 29860.08 | Diameter | 150 | mm
[5 empty] | Length | 3 | m
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | each
Ultrasonic Level | DWW - Dirty Wash Water Handling | 2 | New | 4789.8121 | Qty | 2 | each
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 2 | number
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 2 | New | 22494.6574 | Nominal Bore | 150 | mm
[5 empty] | Installation Complexity | Complex
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 18260.1 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
| Total Asset direct costs |  |  | 260934.042
Location Factors
| Site wide Electrical Distribution |  |  | 15003.71 | Power to new assets
| Are specialist scaffolding resources required to access assets? |  |  | 10689.86 | required for asset installation
| Total Location Factor Costs |  |  | 25693.57
| On Cost |  |  | 132486.34
| Grand Total |  |  | 419113.952
Investment Code | I043768
Investment Title | SUE25 Baylham WWSupernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty | 1 | unit
Electrical Actuator | DWW - Dirty Wash Water Handling | 2 | New | 12349.2896 | Valve Size | 150 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 4 | New | 5005.1135 | Nominal Bore | 225 | m
Tank Cover <#2> | RWS - Raw Water Storage | 1 | New | 15204.5798 | Cover Plan Area | 25 | m2
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 21303.45 | Diameter | 150 | mm
[5 empty] | Length | 35 | m
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 1 | Replacement | 14930.04 | Diameter | 150 | mm
[5 empty] | Length | 3 | m
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | each
Ultrasonic Level | DWW - Dirty Wash Water Handling | 1 | New | 2394.9061 | Qty | 1 | unit
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 1 | number
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 2 | New | 22494.6574 | Nominal Bore | 150 | mm
[5 empty] | Installation Complexity | Complex
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 18260.1 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
| Total Asset direct costs |  |  | 185017.5139
Location Factors
| Site wide Electrical Distribution |  |  | 10638.51 | Power to new assets
| Are specialist scaffolding resources required to access assets? |  |  | 7579.74 | required for asset access to install
| Total Location Factor Costs |  |  | 18218.25
| On Cost |  |  | 95372.5
| Grand Total |  |  | 298608.2639
Investment Code | I043775
Investment Title | NBR9Carbrooke WW Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty | 1 | unit
Electrical Actuator | DWW - Dirty Wash Water Handling | 6 | New | 41449.3595 | Valve Size | 200 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 6 | New | 7510.2375 | Nominal Bore | 200 | mm
Installation Complexity
Closed Rectangular Tank (Sloped Floor) | DWW - Dirty Wash Water Handling | 2 | New | 431069.1347 | Volume | 200 | m3
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 132082.24 | Diameter | 200 | mm
[5 empty] | Length | 172 | m
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 2 | New | 21371.1 | Diameter | 150 | mm
[5 empty] | Length | 3 | m
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | each
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Ultrasonic Level | DWW - Dirty Wash Water Handling | 2 | New | 4789.8121 | Qty | 2 | unit
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 2 | New | 1832.8359 | Nominal Bore | 150 | mm
Installation Complexity
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 18260.1 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 2 | number
| Total Asset direct costs |  |  | 731440.1971
Location Factors
| Site wide Electrical Distribution |  |  | 42057.81 | Power to new assets
| Are specialist scaffolding resources required to access assets? |  |  | 29965.41 | access to asset installation
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 19830.57 | Make safe current tanks
| Total Location Factor Costs |  |  | 91853.79
| On Cost |  |  | 363283.43
| Grand Total |  |  | 1186577.4171
Investment Code | I043756
Investment Title | EXC7 Castle Hedingham WW Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty | 1 | unit
Electrical Actuator | DWW - Dirty Wash Water Handling | 2 | New | 12349.2896 | Valve Size | 150 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 6 | New | 9931.4741 | Nominal Bore | 250 | mm
[5 empty] | Installation Complexity | non complex
Tank Cover <#2> | RWS - Raw Water Storage | 1 | New | 55412.8494 | Cover Plan Area | 76 | m2
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 36520.2 | Diameter | 150 | mm
[5 empty] | Length | 60 | m
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 2 | Replacement | 29860.08 | Diameter | 150 | mm
[5 empty] | Length | 3 | m
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | each
Ultrasonic Level | DWW - Dirty Wash Water Handling | 2 | New | 4789.8121 | Qty | 2 | unit
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 2 | number
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 2 | New | 22494.6574 | Nominal Bore | 150 | mm
[5 empty] | Installation Complexity | Complex
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 18260.1 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
| Total Asset direct costs |  |  | 262693.8401
Location Factors
| Site wide Electrical Distribution |  |  | 15104.9 | Power to new assets
| Are specialist scaffolding resources required to access assets? |  |  | 10761.96 | req for asset access
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 12627.19 | Removal of existing covers
| Total Location Factor Costs |  |  | 38494.05
| On Cost |  |  | 138913.26
| Grand Total |  |  | 440101.1501
Investment Code | I043777
Investment Title | NED3 Dereham WW Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty | 1 | unit
Electrical Actuator | DWW - Dirty Wash Water Handling | 2 | New | 12349.2896 | Valve Size | 150 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 8 | New | 10010.2271 | Nominal Bore | 25 | m
[5 empty] | Installation Complexity | non-Complex
Tank Cover <#2> | RWS - Raw Water Storage | 1 | New | 173672.4657 | Cover Plan Area | 226 | m2
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 42606.9 | Diameter | 150 | mm
[5 empty] | Length | 70 | m
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 3 | Replacement | 44790.12 | Diameter | 150 | mm
[5 empty] | Length | 3 | m
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | each
Ultrasonic Level | DWW - Dirty Wash Water Handling | 3 | New | 7184.7182 | Qty |  | unit
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 2 | number
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 3 | New | 33741.9861 | Nominal Bore | 150 | mm
[5 empty] | Installation Complexity | Complex
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 18260.1 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
| Total Asset direct costs |  |  | 415691.1841
Location Factors
| Site wide Electrical Distribution |  |  | 23902.24
| Are specialist scaffolding resources required to access assets? |  |  | 17029.9
| Total Location Factor Costs |  |  | 40932.14
| On Cost |  |  | 206781.94
| Grand Total |  |  | 663405.2641
Investment Code | I025501
Investment Title | FND26 Hillington Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty | 1 | unit
Electrical Actuator | DWW - Dirty Wash Water Handling | 2 | New | 12349.2896 | Valve Size | 150 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 8 | New | 10013.65 | Nominal Bore | 200 | mm
[5 empty] | Installation Complexity | non-Complex
Tank Cover <#2> | RWS - Raw Water Storage | 2 | New | 109248.9039 | Cover Plan Area | 75 | m2
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 16678.4 | Length | 40 | m
[5 empty] | Diameter | 150 | mm
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 3 | Replacement | 44790.12 | Length | 3 | m
[5 empty] | Diameter | 150 | mm
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | unit
Ultrasonic Level | DWW - Dirty Wash Water Handling | 3 | New | 7184.7182 | Qty | 3 | number
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 2 | number
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 3 | New | 2749.2538 | Diameter | 150 | mm
[5 empty] | Installation Complexity | non-Complex
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 12508.8 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
| Total Asset direct costs |  |  | 288598.5129
Location Factors
| Site wide Electrical Distribution |  |  | 16594.41 | Power to new assets
| Are specialist scaffolding resources required to access assets? |  |  | 11823.21 | required for asset access
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 13149.54 | Remove existing covers
| Total Location Factor Costs |  |  | 41567.16
| On Cost |  |  | 151664.1
| Grand Total |  |  | 481829.7729
Investment Code | I025509
Investment Title | EXS7 Gt Horkesley Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty |  | unit
Electrical Actuator | DWW - Dirty Wash Water Handling | 2 | New | 12349.2896 | Valve Size | 150 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 6 | New | 24474.2969 | Nominal Bore | 400 | mm
[5 empty] | Installation Complexity | non-Complex
Tank Cover <#2> | RWS - Raw Water Storage | 4 | New | 234265.7566 | Cover Plan Area | 80 | m2
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 20848 | Diameter | 150 | mm
[5 empty] | Length | 50 | m
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 2 | Replacement | 29860.08 | Diameter | 150 | mm
[5 empty] | Length | 3 | m
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | each
Ultrasonic Level | DWW - Dirty Wash Water Handling | 2 | New | 4789.8121 | Qty |  | unit
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 1 | number
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 2 | New | 1832.8359 | Nominal Bore | 150 | mm
Installation Complexity
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 12508.8 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
| Total Asset direct costs |  |  | 414004.2486
Location Factors
| Site wide Electrical Distribution |  |  | 23805.24 | Power to new assets
| Are specialist scaffolding resources required to access assets? |  |  | 16960.79 | req for asset install
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 15362.18 | Removal of existing covers
| Total Location Factor Costs |  |  | 56128.21
| On Cost |  |  | 212626.61
| Grand Total |  |  | 682759.0686
Investment Code | I043767
Investment Title | NNC5 Metton WW Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty | 1 | unit
Electrical Actuator | DWW - Dirty Wash Water Handling | 2 | New | 12349.2896 | Valve Size | 150 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 6 | New | 12840.0387 | Nominal Bore | 280 | m
[5 empty] | Installation Complexity | non-Complex
Tank Cover <#2> | RWS - Raw Water Storage | 4 | New | 188538.705 | Cover Plan Area | 65.5 | m2
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 24346.8 | Diameter | 150 | mm
[5 empty] | Length | 40 | m
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 2 | Replacement | 29860.08 | Diameter | 150 | mm
[5 empty] | Length | 3 | m
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | each
Ultrasonic Level | DWW - Dirty Wash Water Handling | 2 | New | 4789.8121 | Qty | 1 | unit
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 2 | number
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 2 | New | 22494.6574 | Nominal Bore | 150 | mm
[5 empty] | Installation Complexity | Complex
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 18260.1 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
| Total Asset direct costs |  |  | 386554.8602
Location Factors
| Site wide Electrical Distribution |  |  | 22226.9 | Power to new assets
| Are specialist scaffolding resources required to access assets? |  |  | 15836.26 | req for asset installation access
| Total Location Factor Costs |  |  | 38063.16
| On Cost |  |  | 192904.15
| Grand Total |  |  | 617522.1702
Investment Code | I043762
Investment Title | NAY5 Royston Bridge WW Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty | 1 | unit
Electrical Actuator | DWW - Dirty Wash Water Handling | 2 | New | 12349.2896 | Valve Size | 150 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 6 | New | 7510.2375 | Nominal Bore | 200 | m
[5 empty] | Installation Complexity | non-Complex
Tank Cover <#2> | RWS - Raw Water Storage | 1 | New | 58566.4392 | Cover Plan Area | 80 | m2
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 24346.8 | Diameter | 150 | mm
[5 empty] | Length | 40 | m
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 2 | Replacement | 29860.08 | Diameter | 150 | mm
[5 empty] | Length | 3 | m
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | each
Ultrasonic Level | DWW - Dirty Wash Water Handling | 2 | New | 4789.8121 | Qty | 2 | unit
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 2 | number
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 2 | New | 22494.6574 | Nominal Bore | 150 | mm
[5 empty] | Installation Complexity | Complex
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 18260.1 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
| Total Asset direct costs |  |  | 251252.7932
Location Factors
| Site wide Electrical Distribution |  |  | 14447.04 | Power to new assets
| Are specialist scaffolding resources required to access assets? |  |  | 10293.24 | req for asset install
| Total Location Factor Costs |  |  | 24740.28
| On Cost |  |  | 127783.19
| Grand Total |  |  | 403776.2632
Investment Code | I043757
Investment Title | NHL7 Rushall WW Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4076.8812 | Diameter | 100 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty | 1 | unit
Electrical Actuator | DWW - Dirty Wash Water Handling | 6 | New | 31626.2348 | Valve Size | 100 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 6 | New | 3486.7779 | Nominal Bore | 100 | m
[5 empty] | Installation Complexity | non-Complex
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 35733 | Diameter | 100 | mm
[5 empty] | Length | 100 | m
Pumping Station | DWW - Dirty Wash Water Handling | 1 | New | 224844.3399 | Total Installed Power | 20 | kW
[5 empty] | Sump Volume | 10 | m3
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 1 | New | 10719.9 | Diameter | 100 | mm
[5 empty] | Length | 30 | m
Polyelectrolyte Dosing | 1D - Suspended Solids Removal | 1 | New | 121810.14 | Flow | 1 | Ml/d
PLC | DWW - Dirty Wash Water Handling | 1 | New | 13508.4823 | In/Out Cards | 2 | number
Submersible Pump | RWP - Raw Water Pumping | 2 | New | 16653.1548 | Pump Rating | 7.5 | kW
Chamber | DWW - Dirty Wash Water Handling | 1 | New | 35161.1294 | Volume | 12 | m3
Ferric Dosing | 1D - Suspended Solids Removal | 1 | New | 45241.4516 | Flow (Ml/d) | 12 | Ml/d
Rectangular Tank | CLA - Clarification | 1 | New | 108892.0981 | Volume | 50 | m3
Platform | CLA - Clarification | 1 | New | 51982.7399 | Area | 20 | m2
Steps | CLA - Clarification | 1 | New | 8729.9737 | Height | 2 | m
Handrail | CLA - Clarification | 1 | New | 10155.9472 | Length | 30 | m
Rigid Pipework <#3> | CLA - Clarification | 1 | New | 35733 | Diameter | 100 | mm
[5 empty] | Length | 100 | m
Rigid Pipework <#5> | CLA - Clarification | 1 | New | 7151.1 | Diameter | 400 | mm
[5 empty] | Length | 10 | m
Centrifugal Horiz | CLA - Clarification | 1 | New | 9207.8833 | Pump Rating | 3 | kW
Reflux Valve | CLA - Clarification | 1 | New | 3370.3793 | Nominal Bore | 150
Probes (Level) | CLA - Clarification | 3 | New | 5559.6978
DC Motor | CLA - Clarification | 1 | New | 9908.2742 | Total Installed Power | 3 | kW
Star Delta Starter | CLA - Clarification | 1 | New | 10256.4918 | Total Installed Power | 3 | kW
Davit Socket | SBS - Site Services | 1 | New | 1900.2887 | Safe Working Load | 750 | kg
Davit | SBS - Site Services | 1 | New | 8298.5331 | Safe Working Load | 750 | kg
Rigid Pipework <#4> | CLA - Clarification | 1 | New | 7151.1 | Diameter | 400 | mm
[5 empty] | Length | 10 | m
Kiosk-LPCB3 | SBS - Site Services | 1 | New | 53841.6648 | Footprint Area | 15 | m2
Kiosk <#2>-LPCB3 | SBS - Site Services | 1 | New | 53841.6648 | Footprint Area | 15 | m3
Landscaping | SBS - Site Services | 1 | Refurbishment | 4636.1483 | Area | 50 | m2
Telemetry Outstation-MM4 | TEL - Telemetry | 1 | Refurbishment | 7565.1207 | Qty | 1 | unit
PLC <#2> | POL - Polyelectrolyte Dosing | 1 | New | 15058.1743 | In/Out Cards | 2 | number
PLC <#3> | FER - Ferric Dosing | 1 | New | 15058.1743 | In/Out Cards | 2 | number
Rigid Pipework <#6> | DWW - Dirty Wash Water Handling | 2 | New | 17323.2 | Diameter | 100 | mm
[5 empty] | Length | 3 | m
covering supernatant tanks |  | 2 | New | 247000
| Total Asset direct costs |  |  | 1243137.7197
| On Cost |  |  | 538685.73
| Grand Total |  |  | 1781823.4497
Investment Code | I043761
Investment Title | NNC6 Sheringham WW Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Magflow | DWW - Dirty Wash Water Handling | 1 | New | 4842.3941 | Diameter | 150 | mm
Turbidity Monitor | DWW - Dirty Wash Water Handling | 1 | New | 7654.5733 | Qty | 1 | unit
Electrical Actuator | DWW - Dirty Wash Water Handling | 2 | New | 12349.2896 | Valve Size | 150 | mm
Gate Valve | DWW - Dirty Wash Water Handling | 8 | New | 19705.4423 | Nominal Bore | 300 | m
[5 empty] | Installation Complexity | non-Complex
Tank Cover <#2> | RWS - Raw Water Storage | 7 | New | 376852.3815 | Cover Plan Area | 74 | m2
Rigid Pipework | DWW - Dirty Wash Water Handling | 1 | New | 60867 | Diameter | 150 | mm
[5 empty] | Length | 100 | m
Rigid Pipework <#2> | DWW - Dirty Wash Water Handling | 3 | Replacement | 44790.12 | Diameter | 150 | mm
[5 empty] | Length | 3 | m
Scada | DWW - Dirty Wash Water Handling | 1 | New | 17191.0991 | Memory Capacity | 1 | GB
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | each
Ultrasonic Level | DWW - Dirty Wash Water Handling | 3 | New | 7184.7182 | Qty | 2 | unit
PLC | DWW - Dirty Wash Water Handling | 1 | New | 15358.3903 | In/Out Cards | 2 | number
Submersible Pump | DWW - Dirty Wash Water Handling | 2 | New | 14385.8782 | Pump Rating | 5 | kW
Gate Valve <#2> | DWW - Dirty Wash Water Handling | 2 | New | 22494.6574 | Nominal Bore | 150 | mm
[5 empty] | Installation Complexity | Complex
Rigid Pipework <#3> | DWW - Dirty Wash Water Handling | 1 | New | 18260.1 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
| Total Asset direct costs |  |  | 635579.0864
Location Factors
| Are the works in a town centre/heavily congested area? |  |  | 41066.83
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 18479.48 | Removal of existing cover
| Site wide Electrical Distribution |  |  | 36545.8 | Power to new assets
| Are specialist scaffolding resources required to access assets? |  |  | 26038.2 | required for asset install
| Total Location Factor Costs |  |  | 122130.31
| On Cost |  |  | 335567.29
| Grand Total |  |  | 1093276.6864
Investment Code | I043772
Investment Title | LNE3 Covenham Supernatant Return DD
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Polyelectrolyte Dosing | 1D - Suspended Solids Removal | 1 | New | 127840.0632 | Flow | 1.6 | Ml/d
Telemetry | SS - Site Services | 1 | New | 54572.1703 | Number of Telemetry Outstations | 4 | each
Washwater Pressure Pipelines | SS - Site Services | 1 | New | 4718.2312 | Length | 30 | m
Interstage Pumping | 1G - Final Water Conditioning | 1 | New | 221468.003 | Total Installed Power (inc standby) | 3.3 | kW
Kiosks-LPBC3 | SS - Site Services | 1 | New | 16401.771 | Area | 4 | m2
Sludge Mixers - M&E | 2G - Sludge Centre | 1 | New | 111585.5935 | Total Volume | 150 | m3
Rigid Pipework | SBS - Site Services | 1 | New | 102296.4946 | Diameter | 150 | mm
[5 empty] | Length | 30 | m
Interstage Pumping <#2> | 1G - Final Water Conditioning | 1 | New | 221468.003 | Total Installed Power (inc standby) | 3.3 | kW
Rigid Pipework <#2> | SBS - Site Services | 1 | New | 25549.0336 | Diameter | 50 | mm
[5 empty] | Length | 230 | m
Pumps, Washwater - M&E | 2A - Catchment Pumping | 1 | New | 62833.9481 | Total Installed Power (inc standby) | 3.3 | kW
Pumps, Washwater - M&E <#2> | 2A - Catchment Pumping | 1 | New | 62833.9481 | Total Installed Power (inc standby) | 3.3 | kW
Clarifiers | 1D - Suspended Solids Removal | 1 | New | 2500671.431 | Flow | 2.3 | Ml/d
Turbidity Monitor | SLK - Sludge Thickening | 1 | New | 7654.5733 | Qty | 1 | unit
| Total Asset direct costs |  |  | 3519893.264
Location Factors
| Are temporary works required to keep the existing plant operational? |  |  | 61366.17
| Does the solution need modelling prior to delivery? |  |  | 13095.5
| Total Location Factor Costs |  |  | 74461.67
| On Cost |  |  | 1486444.54
| Grand Total |  |  | 5080799.474
Investment Code | I041169 and I041168
Investment Title | FND22a Marham surface water abstraction relocation
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unity of Measurement
Rigid Pipework <#4> | RWP - Raw Water Pumping | 1 | New | 166874 | Diameter (mm) | 500 | mm
[5 empty] | Length | 200 | m
Membrane Filters | 1D - Suspended Solids Removal | 1 | New | 638638.9502 | Flow | 13.6 | Ml/d
Rigid Pipework <#5> | INT - Interstage Pumping | 1 | New | 83437 | Diameter (mm) | 500 | mm
[5 empty] | Length | 100 | m
Interstage Pumping | 1G - Final Water Conditioning | 1 | New | 877198.4 | Total Installed Power (inc standby) | 186 | kW
Pre & Post Ozone | 1E - Soluble Compounds / Hydrocarbon Removal | 1 | New | 2358679.804 | Flow | 13.6 | Ml/d
Maximum Water Capacity | 1K - Treated Water Storage | 1 | New | 2016639.86 | Total Volume | 3250 | m3
Telemetry | SS - Site Services | 1 | New | 40929.1277 | Number of Telemetry Outstations | 3 | number
Site Security CCTV | SS - Site Services | 1 | New | 59661.7034 | Flow | 13.6 | Ml/d
[5 empty] | Number of cameras | 5 | unit
Boundary Fencing | SS - Site Services | 1 | New | 319550.2193 | Length | 400 | m
Standby Generation <#2> | SS - Site Services | 1 | New | 319500.9283 | Total Installed Power | 500 | kW
Scada | TWS - Treated Water Storage | 1 | New | 58180.432 | Memory Capacity 100 |  | GB
PLC <#2> | TWS - Treated Water Storage | 1 | New | 62027.6831 | In/Out Cards | 20 | number
Fittings <#3>Sluice | 01 - AW Water Infra | 2 | New | 80052 | Main Diameter | 400 | mm
Combined DAF | 1D - Suspended Solids Removal | 1 | New | 4060598.726 | Flow | 13.6 | Ml/d
Interstage Pumping <#2> | 1G - Final Water Conditioning | 1 | New | 547000.28 | Total Installed Power (inc standby) | 94 | kW
Landscaping <#2> | SS - Site Services | 1 | New | 164038.9853 | Area | 7500 | m2
Buildings <#2> Ozone Process | SS - Site Services | 1 | New | 333172.2938 | Footprint Area | 150 | m3
Buildings- Membrane process | SS - Site Services | 1 | New | 603315.2347 | Footprint Area | 300 | m4
Buildings <#3> DAF building | SS - Site Services | 1 | New | 513267.5877 | Footprint Area | 250 | m5
Buildings <#4> Generator | SS - Site Services | 1 | New | 135067.4705 | Footprint Area | 40 | m6
Reservoir Infrastructure and Landscaping | 1K - Treated Water Storage | 1 | New | 94432.21 | Area | 1500 | m2
Roads | SS - Site Services | 1 | New | 130373.0957 | Area | 1050 | m2
Biodiversity Net Gain | SS - Site Services | 1 | New | 26400 | Biodiversity Units | 0.88 | unit
Water Main | 01 - AW Water Infra | 1 | New | 8312270.3894 | Diameter (mm) | 441 | mm
[5 empty] | Depth | 1200 | mm
[5 empty] | Length in Verge/Unmade (m) | 58 | m
[5 empty] | Length in Field (m) | 11761 | m
[5 empty] | Length in Path (m) | 7 | m
Water Main <#3> | 01 - AW Water Infra | 1 | New | 547419.906 | Diameter (mm) | 441 | mm
[5 empty] | Depth | 10001 | mm
[5 empty] | Length of Directional Drill Complex | 218 | m
Landscaping <#2> | SS - Site Services | 1 | New | 106230.0119 | Area | 4000 | m2
Roads <#2> | SS - Site Services | 1 | New | 68774.2596 | Area | 500 | m2
Boundary Fencing | SS - Site Services | 1 | New | 169647.8635 | Length | 200 | m2
Water Main <#2> | 01 - AW Water Infra | 1 | New | 459531.389 | Diameter (mm) | 441 | mm
[5 empty] | Depth | 10001 | mm
[5 empty] | Length of Directional Drill Complex | 183 | m
Water Main <#4> | 01 - AW Water Infra | 1 | New | 1427990.9427 | Diameter (mm) | 441 | mm
[5 empty] | Depth | 1200 | mm
[5 empty] | Length in Type 3/4 Reinstatement (m) | 1029 | m
Standby Generation | SS - Site Services | 1 | New | 156353.8 | Total Installed Power | 117 | kW
Raw Water Pumps - Civil | 1C - Raw Water Transfer | 1 | New | 677376.3784 | Total Installed Power (inc standby) | 234 | kW
Raw Water Pumps - M&E | 1C - Raw Water Transfer | 1 | New | 609432.6918 | Total Installed Power (inc standby) | 234 | kW
Telemetry | SS - Site Services | 1 | New | 13643.0426 | Number of Telemetry Outstations | 1 | unit
Reservoir Abstraction | 1A - Abstraction | 1 | New | 1162983.54 | Total Installed Power (inc standby) | 108 | kW
Biodiversity Net Gain | SS - Site Services | 1 | New | 36000 | Biodiversity Units | 1.2 | unit
| Total Asset direct costs |  |  | 27436690.2066
| Site wide Electrical Distribution |  |  | 787119.57
Location Factors
| Are temporary works required to keep the existing plant operational? |  |  | 252378.75 | during commissioning and connections
| Do AWS need to purchase / rent additional land to enable the scheme to be delivered? |  |  | 444378.33 | new WTW located to west of existing site
| Does the site have a high water table - does it need dewatering? |  |  | 1194402.59 | lowlying fenland location - will likely need dewatering
| Does the site have poor ground conditions - does it need piling? |  |  | 387960.97 | lowlying fenland location - upper strata of ground in the area is weak and will likely need piling
| Does the solution need modelling prior to delivery? |  |  | 91906.93 | process modelling
| Does the solution require an extensive planning effort? |  |  | 1953319.64
| Does the solution require environmental mitigation measures to be implemented? |  |  | 700896.28 | New WTW with buildings . built on new land adjacent existing WTW - linked to pipeline to new Intake on River Nar - Planning +EIA + Environmental investigations
| Does the statutory power supply need upgrading? |  |  | 551416.08 | Major MEICA installation
| Is an Environmental Impact Assessment (EIA) report required? |  |  | 592700.01 | New WTW with buildings . built on new land adjacent existing WTW - linked to pipeline to new Intake on River Nar - Planning +EIA + Environmental investigations
| Is an archaeological study required? |  |  | 636820.02
| Is existing site demolition / enabling works required to allow the solutions to be realised? |  |  | 371132.63 | decomissioning of existing WTW assets
| Do the works cross other significant infrastructure - rail lines, open water, major roads, medium and high pressure gas lines? |  |  | 62373.08
| Total Location Factor Costs |  |  | 8026804.88
| On Cost |  |  | 7547605.64
| Grand Total |  |  | 43011100.7266

## Nutrient Removal Cost Breakdown
Investment ID | I038949
Investment Title | Hail Weston WRC WFD_IMP P > 1mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5 | m
[5 empty] | Diameter | 150 | mm
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15 | m
[5 empty] | Usage | Process
[5 empty] | Diameter | 150 | mm
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500 | m
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150 | mm
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1 | m3
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8 | kW
Natural Capital Wetland | 2H - Tertiary Treatment | 2 | New | 1197274.24 | Area | 14630 | m2
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150 | mm
Kiosks | SS - Site Services | 1 | New | 30988.461 | Security Level | Low
[5 empty] | Area | 10 | m2
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30 | m2
Boundary Fencing | SS - Site Services | 1 | New | 122377.2568 | Security Level | General
[5 empty] | Length | 684 | m
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 1843169.07
|  |  | Permit Cost | 3019
|  |  | Site wide Electrical Distribution at WRC | 106155.81
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 398814.41
|  |  | On Cost | 634577.62
|  |  | Grand Total CAPEX | 2985735.92
Investment ID | I038950
Investment Title | Morcott WRC WFD_IMP P > 1mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5 | m
[5 empty] | Diameter | 150 | mm
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15 | m
[5 empty] | Usage | Process
[5 empty] | Diameter | 150 | mm
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500 | m
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150 | mm
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1 | m3
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8 | kW
Natural Capital Wetland | 2H - Tertiary Treatment | 1 | New | 550333.832 | Area | 13068 | m2
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150 | mm
Kiosks | SS - Site Services | 1 | New | 30988.461 | Security Level | Low
[5 empty] | Area | 10 | m2
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30 | m2
Boundary Fencing | SS - Site Services | 1 | New | 82755.527 | Security Level | General
[5 empty] | Length | 457 | m
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 1156606.93
|  |  | Permit Cost | 3019
|  |  | Site wide Electrical Distribution at WRC | 66678.49
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 215904.08
|  |  | On Cost | 389252.07
|  |  | Grand Total CAPEX | 1831460.57
Investment ID | I038952
Investment Title | Westbury WRC WFD_IMP P > 1mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5 | m
[5 empty] | Diameter | 150 | mm
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15 | m
[5 empty] | Usage | Process
[5 empty] | Diameter | 150 | mm
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500 | m
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150 | mm
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1 | m3
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8 | kW
Natural Capital Wetland | 2H - Tertiary Treatment | 2 | New | 1265307.04 | Area | 15730 | m2
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150 | mm
Kiosks | SS - Site Services | 1 | New | 30988.461 | Security Level | Low
[5 empty] | Area | 10 | m2
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30 | m2
Boundary Fencing | SS - Site Services | 1 | New | 126740.8834 | Security Level | General
[5 empty] | Length | 709 | m
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 1915565.5
|  |  | Permit Cost | 3019
|  |  | Site wide Electrical Distribution at WRC | 110318.61
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 420924.43
|  |  | On Cost | 661208.45
|  |  | Grand Total CAPEX | 3111035.99
Investment ID | I038962
Investment Title | Shouldham WRC WFD_ND Growth P > 1mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5 | m
[5 empty] | Diameter | 150 | mm
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15 | m
[5 empty] | Usage | Process
[5 empty] | Diameter | 150 | mm
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500 | m
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150 | mm
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1 | m3
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8 | kW
Natural Capital Wetland | 2H - Tertiary Treatment | 1 | New | 848317.5 | Area | 22704 | m2
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150 | mm
Kiosks | SS - Site Services | 1 | New | 30988.461 | Security Level | Low
[5 empty] | Area | 10 | m2
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30 | m2
Boundary Fencing | SS - Site Services | 1 | New | 108239.11 | Security Level | General
[5 empty] | Length | 603 | m
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 1480074.17
|  |  | Permit Cost | 3019
|  |  | Site wide Electrical Distribution at WRC | 85277.86
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 314139.65
|  |  | On Cost | 508089.63
|  |  | Grand Total CAPEX | 2390600.32
Investment ID | I040380
Investment Title | Stibbard WRC HD_IMP P >1mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5
[5 empty] | Diameter | 150
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15
[5 empty] | Usage | Process
[5 empty] | Diameter | 150
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8
Natural Capital Wetland | 2H - Tertiary Treatment | 1 | New | 436038.728 | Area | 9372
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150
Kiosks | SS - Site Services | 1 | New | 30988.461 | Security Level | Low
[5 empty] | Area | 10
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30
Boundary Fencing | SS - Site Services | 1 | New | 70537.37 | Security Level | General
[5 empty] | Length | 387
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 1030093.67
|  |  | Permit Cost | 3019
|  |  | Site wide Electrical Distribution at WRC | 59403.98
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 182731.76
|  |  | On Cost | 344189.55
|  |  | Grand Total CAPEX | 1619437.96
Investment ID | I040629
Investment Title | Grasby WRC EnvAct_Imp1 P 1mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5 | m
[5 empty] | Diameter | 150 | mm
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15 | m
[5 empty] | Usage | Process
[5 empty] | Diameter | 150 | mm
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500 | m
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150 | mm
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1 | m3
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8 | kW
Natural Capital Wetland | 2H - Tertiary Treatment | 1 | New | 705448.616 | Area | 18084 | m2
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150 | mm
Kiosks | SS - Site Services | 1 | New | 30988.461 | Security Level | Low
[5 empty] | Area | 10 | m2
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30 | m2
Boundary Fencing | SS - Site Services | 1 | New | 96893.6773 | Security Level | General
[5 empty] | Length | 538 | m
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 1325859.87
|  |  | Permit Cost | 3019
|  |  | Site wide Electrical Distribution at WRC | 76410.53
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 265864.2
|  |  | On Cost | 451044.36
|  |  | Grand Total CAPEX | 2122197.95
Investment ID | I041718
Investment Title | West by Welland WFD _IMP P 2.5mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5 | m
[5 empty] | Diameter | 150 | mm
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15 | m
[5 empty] | Usage | Process
[5 empty] | Diameter | 150 | mm
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500 | m
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150 | mm
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1 | m3
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8 | kW
Natural Capital Wetland | 2H - Tertiary Treatment | 1 | New | 831989.624 | Area | 22176 | m2
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150 | mm
Kiosks | SS - Site Services | 1 | New | 30988.461 | Security Level | Low
[5 empty] | Area | 10 | m2
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30 | m2
Boundary Fencing | SS - Site Services | 1 | New | 107017.2911 | Security Level | General
[5 empty] | Length | 596 | m
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 1462524.49
|  |  | Permit Cost | 9903.1
|  |  | Site wide Electrical Distribution at WRC | 84664.59
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 308944.87
|  |  | On Cost | 503643.4
|  |  | Grand Total CAPEX | 2369680.44
Investment ID | I041732
Investment Title | Manthorpe WRC WFD_IMP P 1,5mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5 | m
[5 empty] | Diameter | 150 | mm
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15 | m
[5 empty] | Usage | Process
[5 empty] | Diameter | 150 | mm
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500 | m
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150 | mm
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1 | m3
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8 | kW
Natural Capital Wetland | 2H - Tertiary Treatment | 2 | New | 1186388.992 | Area | 14454 | m2
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150 | mm
Kiosks | SS - Site Services | 1 | New | 30988.461 | Security Level | Low
[5 empty] | Area | 10 | m2
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30 | m2
Boundary Fencing | SS - Site Services | 1 | New | 121679.0765 | Security Level | General
[5 empty] | Length | 680 | m
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 1831585.64
|  |  | Permit Cost | 3019
|  |  | Site wide Electrical Distribution at WRC | 105489.77
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 395116.81
|  |  | On Cost | 630273.51
|  |  | Grand Total CAPEX | 2965484.72
Investment ID | I041736
Investment Title | Good Easter WRC WFD_IMP P 3mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5 | m
[5 empty] | Diameter | 150 | mm
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15 | m
[5 empty] | Usage | Process
[5 empty] | Diameter | 150 | mm
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500 | m
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150 | mm
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1 | m3
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8 | kW
Natural Capital Wetland | 2H - Tertiary Treatment | 1 | New | 482301.032 | Area | 10868 | m2
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150 | mm
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30 | m2
Boundary Fencing | SS - Site Services | 1 | New | 75773.7244 | Security Level | General
[5 empty] | Length | 417 | m
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 1050603.87
|  |  | Permit Cost | 3019
|  |  | Site wide Electrical Distribution at WRC | 60583.31
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 190029.36
|  |  | On Cost | 352013.17
|  |  | Grand Total CAPEX | 1656248.71
Investment ID | I041755
Investment Title | Broxted WRC WFD_IMP P 1 mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5 | m
[5 empty] | Diameter | 150 | mm
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15 | m
[5 empty] | Usage | Process
[5 empty] | Diameter | 150 | mm
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500 | m
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150 | mm
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1 | m3
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8 | kW
Natural Capital Wetland | 2H - Tertiary Treatment | 1 | New | 342153.464 | Area | 6336 | m2
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150 | mm
Kiosks | SS - Site Services | 1 | New | 30988.461 | Security Level | Low
[5 empty] | Area | 10 | m2
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30 | m2
Boundary Fencing | SS - Site Services | 1 | New | 75773.7244 | Security Level | General
[5 empty] | Length | 417 | m
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 941444.76
|  |  | Permit Cost | 3019
|  |  | Site wide Electrical Distribution at WRC | 54306.67
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 146601.09
|  |  | On Cost | 309135.77
|  |  | Grand Total CAPEX | 1454507.29
Investment ID | I041757
Investment Title | Arrington WRC WFD_IMP P 1.5mg/l
Name | Functional Location | Quantity | Activity Type | Capital Cost (£) | Attribute | Value | Unit of Measure
Outfall Pipework | FED - Final Effluent Discharge | 1 | New | 12229.8463 | Length | 5 | m
[5 empty] | Diameter | 150 | mm
[5 empty] | Type of Outfall | River
Rigid Pipework <#2> | TER - Tertiary Filtration | 1 | New | 6254.4 | Length | 15 | m
[5 empty] | Usage | Process
[5 empty] | Diameter | 150 | mm
Rigid Pipework | PUM - Inter-Process Pumping | 1 | New | 340988.3153 | Length | 500 | m
[5 empty] | Usage | Rising Main Pipework
[5 empty] | Asset Material | MDPE
[5 empty] | Diameter | 150 | mm
Chamber | SST - Sludge Storage | 1 | New | 7268.5163 | Volume | 1 | m3
Pumping Stations, Interprocess - Civil | 2A - Catchment Pumping | 1 | New | 36326.0324 | Total Installed Power (inc standby) | 8 | kW
Pumps, Raw Sewage/Unthickened Sludge - M&E | 2A - Catchment Pumping | 1 | New | 64893 | Total Installed Power (inc standby) | 8 | kW
Natural Capital Wetland | 2H - Tertiary Treatment | 1 | New | 700005.992 | Area | 17908 | m2
[5 empty] | Liner Type | Bentonite Clay
Magflow | FED - Final Effluent Discharge | 1 | New | 4842.3941 | Diameter | 150 | mm
Kiosks | SS - Site Services | 1 | New | 30988.461 | Security Level | Low
[5 empty] | Area | 10 | m2
Roads | SS - Site Services | 1 | New | 6083.5641 | Area | 30 | m2
Boundary Fencing | SS - Site Services | 1 | New | 96370.0421 | Security Level | General
[5 empty] | Length | 535 | m
Telemetry | SS - Site Services | 1 | New | 13643.0426
|  |  | Total Asset direct costs | 1319893.61
|  |  | Permit Cost | 3019
|  |  | Site wide Electrical Distribution at WRC | 76067.47
|  |  | Total Location Factor Costs (Land, Modelling, Extensive Planning, Environmental Mitigation, Site Demolition/Enabling Works) | 265795.84
|  |  | On Cost | 449323.02
|  |  | Grand Total CAPEX | 2114098.94

## Nutrient and Sanitary (CBA)
Investment Title | Great Casterton WRC WFD_IMP P > 1mg/l
Investment Code | I038945
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Great Casterton WRC Treatment Wetland | 2145750.36 | 2354971.6426 | 306040.7474 | 4.4483 | 182677.2449 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more. AMP9 Delivery
Alternative solution - Great Casterton WRC New dosing plant and ancillaries | 1380643.17 | 1678909.5055 | 180647.9093 | 5.4318 | 92699.0801
Investment Title | Hail Weston WRC WFD_IMP P > 1mg/l
Investment Code | I038949
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Hail Weston WRC Treatment Wetland | 2985735.92 | 3704701.8428 | 410333.4606 | 6.6227 | 216265.0311 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Hail Weston WRC New dosing plant and ancillaries | 1388784.5 | 2067926.17 | 164473.2554 | 9.9658 | 56145.9841
Investment Title | Morcott WRC WFD_IMP P > 1mg/l
Investment Code | I038950
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Morcott WRC Treatment Wetland | 1831460.57 | 2576519.5262 | 281950.6558 | 8.249 | 146981.0614 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Morcott WRC New dosing plant and ancillaries | 1318454.05 | 1908991.1777 | 189072.9566 | 8.9501 | 89071.4149
Investment Title | Shouldham WRC WFD_ND Growth P > 1mg/l
Investment Code | I038962
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Shouldham WRC Treatment Wetland | 2390600.32 | 2988769.55 | 339944.9821 | 6.3231 | 183380.2111 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Shouldham WRC New dosing plant and ancillaries | 981598.71 | 1436197.6839 | 148242.5993 | 7.1421 | 73008.1067 | Site is an RBC works and not conducive to traditional P removal. Therefore Works would require an upgrade to facilitate Iron dosing.
Investment Title | Stibbard WRC HD_IMP P >1mg/l
Investment Code | I040380
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Stibbard WRC Treatment Wetland | 1619437.96 | 2179466.0217 | 234827.6093 | 6.9088 | 120657.5506 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Stibbard WRC New dosing plant and ancillaries | 1728355.87 | 2431049.6023 | 195310.0948 | 9.819 | 67960.7853 | Site is an RBC works <250p.e and not conducive to traditional P removal. Therefore Works would require an upgrade to facilitate Iron dosing.
Investment Title | Grasby WRC EnvAct_Imp1 P 1mg/l
Investment Code | I040629
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Grasby WRC Treatment Wetland | 2122197.95 | 2689103.5825 | 233201.675 | 8.293 | 92334.6213 | AW Strategy to seelct NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Grasby WRC New dosing plant and ancillaries | 785161.45 | 1080049.7958 | 148940.3687 | 5.3458 | 92362.5039
Investment Title | Preston Capes WRC WFD_IMP MOD P 1mg/l
Investment Code | I040701
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Preston Capes WRC Treatment Wetland | 1578484.49 | 2212707.2595 | 428555.9219 | 4.0729 | 312644.454 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Preston Capes WRC New dosing plant and ancillaries | 1980122.09 | 2851649.661 | 247575.3477 | 9.0428 | 98193.1159 | Site is an RBC works <250p.e and not conducive to traditional P removal. Therefore Works would require an upgrade to facilitate Iron dosing.
Investment Title | Good Easter WRC WFD_IMP P 3mg/l
Investment Code | I041736
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Good Easter WRC Treatment Wetland | 1656248.71 | 2221165.7558 | 484093.9294 | 3.4155 | 367739.4314 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Good Easter WRC New dosing plant and ancillaries | 1943406.51 | 2419673.4385 | 347497.5079 | 4.4319 | 220744.1331 | Site is an Oxyjet Process works circa 250p.e and not conducive to traditional P removal. Therefore Works would require an upgrade to facilitate Iron dosing.
Investment Title | Arrington WRC WFD_IMP P 1.5mg/l
Investment Code | I041757
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Arrington WRC Treatment Wetland | 2114098.94 | 2734446.6938 | 479552.356 | 4.2239 | 336310.0507 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Arrington WRC New dosing plant and ancillaries | 1279349.69 | 1553308.8077 | 249721.3735 | 3.6353 | 168352.0736
Investment Title | Broxted WRC WFD_IMP P 1 mg/l
Investment Code | I041755
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Broxted WRC Treatment Wetland | 1454507.29 | 1999386.168 | 462565.8919 | 3.2333 | 357829.1439 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Broxsted WRC New dosing plant and ancillaries | 3828041.73 | 4796050.8579 | 307318.3182 | 8.8741 | 56079.6086 | Site is a Descriptive works and rerquires a major upgrade to facilitate Iron dosing and meet Sanitary parameters
Investment Title | Shudy Camps WRC AMP8 Phased build Wetland for P
Investment Code | I040829
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Shudy Camps WRC Treatment Wetland | 2246411.4 | 3299658.4636 | 445593.3215 | 6.3271 | 272742.6596
Investment Title | West by Welland WFD _IMP P 2.5mg/l
Investment Code | I041718
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - West by Welland WRC Treatment Wetland | 2369680.44 | 3012714.0215 | 512671.1196 | 4.3318 | 354851.9872 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - West by Welland WRC New dosing plant and ancillaries | 1401324.64 | 1690825.9194 | 278141.0083 | 3.5527 | 189567.9438
Investment Title | Manthorpe WRC WFD_IMP P 1,5mg/l
Investment Code | I041732
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Manthorpe WRC Treatment Wetland | 2965484.72 | 3833211.0521 | 421578.4549 | 7.0701 | 542169.0272 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Manthorpe WRC New dosing plant and ancillaries | 812363.11 | 1191113.3909 | 193156.4295 | 4.958 | 130760.5542
Investment Title | Tugby WRC WFD_IMP P > 1mg/l
Investment Code | I038951
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Tugby WRC Treatment Wetland | 1662240.34 | 1895126.6705 | 218737.9966 | 5.036 | 119463.0212 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more. AMP9 Delivery
Alternative solution - Tugby WRC New dosing plant and ancillaries | 1286549.16 | 1558293.1746 | 147268.6688 | 6.1844 | 65638.2653
Investment Title | Northrepps WRC WFD_ND Growth P > 1mg/l
Investment Code | I038955
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Northrepps WRC Treatment Wetland | 2995960.02 | 3154820.9121 | 314922.1772 | 5.7278 | 149659.2939 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more. AMP9 Delivery
Alternative solution - Northrepps WRC New dosing plant and ancillaries | 875866.49 | 1038539.0941 | 119173.0726 | 5.1492 | 64769.725
Investment Title | Earl Soham WRC WFD_ND Growth P > 1mg/l
Investment Code | I038956
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Earl Soham WRC Treatment Wetland | 1888291.89 | 2104504.1432 | 212023.6168 | 5.7381 | 101780.6104 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more. AMP9 Delivery
Alternative solution - Earl Soham WRC New dosing plant and ancillaries | 765053.75 | 918308.9219 | 120105.8038 | 4.5422 | 72000.6532
Investment Title | Sandon WRC WFD_ND Growth P > 1mg/l
Investment Code | I038959
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Sandon WRC Treatment Wetland | 1865496.17 | 2086989.3411 | 210903.8939 | 5.7519 | 101578.3812 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more. AMP9 Delivery
Alternative solution - Sandon WRC New dosing plant and ancillaries | 1974295.56 | 2833806.7432 | 150902.1174 | 14.7436 | 2454.5779
Investment Title | Fincham WRC WFD_ND Growth P > 1mg/l
Investment Code | I038960
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Fincham WRC Treatment Wetland | 2173696.74 | 2379561.2194 | 241876.3833 | 5.6872 | 117224.7682 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more. AMP9 Delivery
Alternative solution - Fincham WRC New dosing plant and ancillaries | 1436922.72 | 1758175.5149 | 116302.3613 | 8.8359 | 24201.2221
Investment Title | Barton Bendish WRC WFD_ND Growth P > 1mg/l
Investment Code | I038961
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Barton Bendish WRC Treatment Wetland | 2145092.55 | 2351892.0432 | 242007.7353 | 5.618 | 118805.5561 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more. AMP9 Delivery
Alternative solution - Barton Bendish WRC New dosing plant and ancillaries | 1242862.58 | 1535553.7399 | 116940.5816 | 7.7168 | 36501.372
Investment Title | Benefield WRC WFD_ND Growth P > 1mg/l
Investment Code | I038963
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Benefield WRC Treatment Wetland | 1995927.82 | 2208180.5469 | 190456.9332 | 6.702 | 329481.1138 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more. AMP9 Delivery
Alternative solution - Benefield WRC New dosing plant and ancillaries | 1304923.08 | 1915746.4139 | 157837.8781 | 9.6206 | 57482.4667
Investment Title | Gipsey Bridge WRC WFD_ND Growth P > 1mg/l
Investment Code | I038968
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Gipsey Bridge WRC Treatment Wetland | 2348407.92 | 2540197.23 | 636940.5503 | 2.2927 | 503873.5973 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more. AMP9 Delivery
Alternative solution - Gipsey Bridge WRC New dosing plant and ancillaries | 2068412.39 | 2370629.3759 | 111215.1621 | 12.3237 | -12969.0642
Investment Title | Westbury WRC WFD_IMP P > 1mg/l
Investment Code | I038952
Option | Capex | Whole Life Cost | Equivalent Annualised Benefit | Risk Index | Equivalent Annualiased Value | Explanation
Preferred option - Westbury WRC Treatment Wetland | 3111035.99 | 3846420.5995 | 1014665.9413 | 2.7807 | 813173.6857 | AW Strategy to select NBS where appropriate with this site meeting the EA guidelines parameters of less than 1000 p.e and 1mg/l P limit or more.
Alternative solution - Westbury WRC New dosing plant and ancillaries | 1440146.8 | 2139060.8429 | 794381.1617 | 2.1342 | 682327.5363