## EDM Return for Anglian Water
EDM Return for Anglian Water
Period selected from 01/05/2021 to 30/09/2021
Water Company Name | Site Name | Outlet discharge NGR 1 | Outlet discharge NGR 2 | Permit No. | Activity Reference (if more than one discharge) on permit | Initial EDM commission date | Shellfishery (Only populate for storm overflows that have Shellfish water EDM requirements) | Bathing Beach (Only populate for storm overflows that have bathing water EDM requirements) | Total Duration (hours) of all spills prior to processing through 12-24 hour counting method | Counted spills using 12-24hr counting method | % of reporting period EDM operational | Comments
Anglian Water | Brightlingsea overflow (Bellfld 35) | TM08121664 |  | ASENF3270/12163/V001 | A1 | 01/04/2018 | N/a | Colne | 1.2 | 4 | 100%
Anglian Water | Brightlingsea overflow - lower park OV | TM08121664 |  | ASENF3270/12162/V001 | A1 | 01/04/2018 | N/a | Colne | 6.5667 | 12 | 99.99%
Anglian Water | Brightlingsea overflow - Station road #58 | TM08121664 |  | ASENF3270/12166/V001 | A1 | 01/04/2018 | N/a | Colne | 6.1333 | 10 | 99.99%
Anglian Water | Brightlingsea overflow (western rd) community centre | TM08121644 |  | ASENF3270/12167/V001 | A1 | 01/04/2018 | N/a | Colne | 1.6 | 7 | 99.99%
Anglian Water | Brightlingsea - West Dyke TPS (Lower Park Road) CSO/EO | TM08121663 |  | ASENF3284/12161/V001 | A1 | 01/04/2018 | N/a | Colne | 2.2667 | 5 | 100%
Anglian Water | Clacton - Collingwood Road / Wash Lane CSO | TM17101391 |  | ASECS12233/V001 | A1 | 01/04/2018 | N/a | Clacton Groyne 41/Clacton Martello Tower | 0.2 | 4 | 99.99%
Anglian Water | CLACTON-GOLF GREEN ROAD CSO 1 | TM15301359 |  | ASETS3332/12240/V001 | A1 | 01/04/2018 | N/a | Jaywick | 0.033333 | 1 | 100%
Anglian Water | Clacton - Kings Parade/Hazlemere Road CSO (Clarendon/Holland overflow) | TM19511535 |  | ASECS3328/12234/V001 | A1 | 01/04/2018 | N/a | Clacton | 0 | 0 | 100%
Anglian Water | Clacton - Park Road/Vicarage Road CSO | TM17101391 |  | ASECS3326/12232/V001 | A1 | 01/04/2018 | N/a | Clacton Groyne 41/Clacton Martello Tower | 0.4 | 2 | 99.99%
Anglian Water | Clacton Seafront CSO/Gunfleet | TM19431551 |  | ASECS3324/12230/V001 | A1 | 01/04/2018 | N/a | Clacton | 10.3 | 1 | 100%
Anglian Water | Clacton STW Storm & EO | TM22261650 | TM22001709 | AEECS/12401/V005 | A2 & A3 | 01/04/2018 | N/a | Holland | 150.5667 | 47 | 99.7% | The spills align with rainfall events.
Anglian Water | Clacton - Victoria Road outfall | TM18531506 |  | AW2CS662/V001 | A1 | 01/04/2018 | N/a | Clacton | 0.83333 | 3 | 100%
Anglian Water | Clacton - West Road TPS | TM16721337 |  | ASECS3325/12231/V001 | A1 | 01/04/2018 | N/a | Clacton Martello Tower | 12.2667 | 6 | 100%
Anglian Water | Cleethorpes Kings Road PS | TA32730664 |  | ANNTS884 | A1 | 01/04/2021 | N/a | Cleethorpes and Humberston Fitties | 0.7 | 1 | 100%
Anglian Water | Cromer Promenade TPS | TG21554244 |  | AEECS868/12071/V001 | A1 | 01/04/2018 | N/a | Cromer | 0 | 0 | 100%
Anglian Water | Frinton on sea - Esplanade/Second Ave CSO | TM23541887 |  | ASECS3309/12191/V001 | A1 | 01/04/2018 | N/a | Frinton | 0.73333 | 1 | 100%
Anglian Water | Frinton on sea - Holland Rd/Second Ave CSO | TM23211934 |  | ASENF3310/12192/V001 | A1 | 01/04/2018 | N/a | Frinton | 0.6 | 1 | 100%
Anglian Water | Frinton on sea - Queens Road/Esplanade CSO | TM24071971 |  | ASECS3311/12194/V001 | A1 | 01/04/2018 | N/a | Frinton | 1.8667 | 1 | 100%
Anglian Water | Frinton - Upper Second Avenue - The Close | TM23031986 |  | ASENF3684/12381/V001 | A1 | 01/04/2018 | N/a | Frinton | 20.0333 | 30 | 100% | Network jetting removed grit from the system. Work completed 12/10/21 and zero spills have been logged since this time.
Anglian Water | Great Yarmouth - Boundary Road Storm PS | TG52420617 |  | AEETS3291/12173/V001 | A1 | 01/04/2018 | N/a | Great Yarmouth South | 0.56667 | 1 | 100%
Anglian Water | Pyewipe Water Recycling Centre & Terminal Pumping Station | TA28281314 |  | AW3TS/519/V003 | A2 | 2021-04-01 | N/a | Cleethorpes | 156.4 | 63 | 99.99% | This storm overflow discharges to the long sea outfall and does not impact the bathing water. The spills align with rainfall events.
Anglian Water | Pyewipe Water Recycling Centre & Terminal Pumping Station | TA26321108 |  | AW3TS/519/V003 | A6 | 2021-04-01 | N/a | Cleethorpes | 31.64 | 20 | 100%
Anglian Water | Gt Yarmouth - Bryants Quay CSO | TG52460687 |  | AEETS3290/12175/V002 | A1 | 01/04/2018 | N/a | Great Yarmouth Pier/Great Yarmouth South | 26.1 | 26 | 99.96% | The spills align with rainfall events. The design standard for Bryants Quay is 26 significant spills per bathing water season.
Anglian Water | Gt Yarmouth-Gorleston - Gt Yarmouth Brush Bend | TG53010372 |  | AEETS/3292/12178/V002 | A1 | 01/04/2018 | N/a | Gorleston Beach | 1.3 | 3 | 100%
Anglian Water | Holland Haven (New) TPS | TM21901720 |  | ASENF2386A | A1 | 01/04/2018 | N/a | Holland |  |  |  | Environment Agency have not yet issued a storm overflow condition under Temporary Deemed Consent project
Anglian Water | HUMBERSTON-BERNERS RD SP | TA31550651 |  | ANNNF3501 | A1 | 01/04/2021 | N/a | Cleethorpes and Humberston Fitties | 0 | 0 | 100%
Anglian Water | Hunstanton - Smugglers Lane ps | TF68734274 |  | ASENF12024/V001 | A1 & A2 | 01/04/2018 | N/a | North West Norfolk | 17.9 | 25 | 81.7% | There are intermittent communication issues at this location. We have been unable to identify the route cause. However since 01/10/21 an improvement has been noted and operational time has been 99.99% since that date.
Anglian Water | Hunstanton Storm Overflow 1 (HUNSTANTON SOUTH END ROAD TPS) | TF66004016 | TF66624002 | AECCS660/10416/V001 | A1 | 01/04/2018 | N/a | Hunstanton Main Beach | 11.7 | 16 | 100%
Anglian Water | Ingoldmells - Southgate Camp | TF57006840 |  | ANNNF2604A | A1 | 01/04/2018 | N/a | Ingoldmells South |  |  |  | Environment Agency have not yet issued a storm overflow condition under Temporary Deemed Consent project
Anglian Water | Ingoldmells (STW) PS | TF57126839 |  | ANNTS3539/13470/V001 | A1 | 01/04/2018 | N/a | Ingoldmells South | 0 | 0 | 100%
Anglian Water | Jaywick - Brooklands Gardens PS | TM14171312 |  | ASENF3334/12238/V001 | A1 | 01/04/2018 | N/a | Jaywick | 0.066667 | 1 | 100%
Anglian Water | Jaywick - Clacton 23 Park Square CSO | TM14651369 |  | ASENF3333/12237/V001 | A1 | 01/04/2018 | N/a | Jaywick | 16.5667 | 10 | 100%
Anglian Water | Lowestoft - Belvedere Road Overflow | TM54449267 |  | ASETS4083/16995/V001 | A1 | 01/04/2018 | N/a | Lowestoft North | 0.5 | 1 | 99.99%
Anglian Water | Lowestoft - Bridge PS | TM54709270 |  | ASETS2159A | A1 | 01/04/2018 | N/a | Lowestoft North |  |  |  | Environment Agency have not yet issued a storm overflow condition under Temporary Deemed Consent project
Anglian Water | LOWESTOFT COMMERICAL RD | TM54819272 |  | ASETS4083/16994/V002 | A1 | 01/04/2018 | N/a | N/a | 0 | 0 | 0% | This storm overflow is no longer in use. The permit is being revoked with the Environment Agency.
Anglian Water | Lowestoft - Marina CSO | TM55139303 |  | ASETS4083/16991/V001 | A1 | 01/04/2018 | N/a | Lowestoft North | 37.2667 | 37 | 99.99% | Tidal influence causes flows to back up into the network via flap valve. Diver investigations have been carried out and we are reviewing the findings to decide the next step.
Anglian Water | Lowestoft - Royal Norfolk & Suffolk Yacht Club (Lowestoft Harbour Bridge SP) | TM54799269 |  | AW4TS12090/V001 | A1 | 01/04/2018 | N/a | Lowestoft North | 16.9 | 20 | 100%
Anglian Water | Lowestoft - Station Square #1 CSO | TM54839280 |  | ASETS4083/16993/V001 | A1 | 01/04/2018 | N/a | Lowestoft North | 6.4 | 17 | 100%
Anglian Water | Lowestoft - Station Square No.2 CSO | TM54809272 |  | EPR/JB3496WZ/V001 | A1 | 01/04/2018 | N/a | Lowestoft North | 1.7333 | 7 | 79.54% | There are intermittent communication issues at this location. We have been unable to identify the route cause. However since 01/10/21 an improvement has been noted and operational time has been 100% since that date.
Anglian Water | Lowestoft - St John's Road CSO | TM54649267 |  | ASETS4082/16950/V001 | A1 | 01/04/2018 | N/a | Lowestoft North | 10.6 | 20 | 100%
Anglian Water | Mablethorpe - George St CSO | TF50618511 |  | ANNNF/892/V001 | A1 | 01/04/2018 | N/a | Mablethorpe Town | 4.7333 | 3 | 99.99%
Anglian Water | Mundesley - The Dell Chalet Park | TG31573649 |  | AEENF791/10515/V001 | A1 | 01/04/2018 | N/a | Mundesley | 0.86667 | 5 | 99.99%
Anglian Water | Mundesley - The Prom PS | TG31663656 |  | AEECS3350/12196/V001 | A1 | 01/04/2018 | N/a | Mundesley | 0 | 0 | 100%
Anglian Water | Sheringham East Beach Sewage Tank (AKA SHERINGHAM BEACH RD TPS) | TG16014347 |  | AEECS867/12070/V001 | A1 | 01/04/2018 | N/a | Sherringham | 0.46667 | 1 | 100%
Anglian Water | Southwold - Gardener Road PS | TM50667582 |  | ASENF91767/10176/V001 | A1 | 01/04/2018 | N/a | Southwold the Deans | 5.7 | 13 | 100%
Anglian Water | Southwold - Marlborough Rd SSO | TM50867691 |  | AW4NF1768v001 | A1 | 01/04/2018 | N/a | Southwold the Pier | 0.63333 | 5 | 100%
Anglian Water | Southwold - Station Rd SSO | TM50347673 |  | AW4NF1762/V001 | A1 | 01/04/2018 | N/a | Southwold the Pier | 0.66667 | 8 | 99.87%
Anglian Water | Walton-on-the-Naze TPS | TM26042227 |  | ASECS3376/12213/V001 | A1 | 01/04/2018 | N/a | Walton | 16.6333 | 10 | 100%
Anglian Water | West Mersea STW SSO | TM03011210 |  | ASETS/1320/V005 | A2 | 01/04/2018 | N/a | West Mersea | 4.8 | 5 | 96.96%